## Slide 1: HESTIA Phase I Results: The Air Revitalization System
Sarah E. Wright
NASA Johnson Space Center
Crew and Thermal Systems Division
Thermal Systems Branch
May 6, 2016

## Slide 2: HESTIA Phase I Test Results: The Air Revitalization System
HESTIA: Human Exploration Spacecraft Testbed for Integration and Advancement
Integrated ECLSS/ISRU testing
  Environmental Control & Life Support Systems
  In-Situ Resource Utilization
Incorporated hardware from various groups in engineering
  Portable CO2 and O2 sensors
  Human Metabolic Simulator
  Electrolyzer
  Air Revitalization System (ARS)
More hardware to be added as technology matures

## Slide 3: Environmental Control and Life Support System (ECLSS)
Crew Systems
Shower
Hand Wash/Shaving
Potable Water Dispenser
Oxygen
H2
Nitrogen
Air
Processed Air
CO2
Water
Product Water
Waste Water
Product Water
Processed Urine
Waste
Condensate
Cabin Return
Cabin Return
Fire Detection
& Suppression
Oxygen Generation
CO2 Removal
Temp & Humidity Control
Potable Water Processing
Urine Recovery
Brine
Brine Product
Brine Water Recovery
Cabin Air
Waste Mgmt
Recovered H2O
TCCS
Vented Waste Gas
Atmosphere Monitors
Brine & Urine Sensors
CO2 Reduction
Particulate Monitor
Acoustic Monitor
Microbial Monitor
(Water & Surfaces)
High P O2
DOES NOT IMPLY SELECTION! PRE-DECISIONAL!
Ag Biocide
PT Urine
Filtration & Heavy VOC Removal
O2/N2 Control
Water Quality Monitors

## Slide 4: Air Revitalization System
Crew Systems
Shower
Hand Wash/Shaving
Potable Water Dispenser
Oxygen
H2
Nitrogen
Air
Processed Air
CO2
Water
Product Water
Waste Water
Product Water
Processed Urine
Waste
Condensate
Cabin Return
Fire Detection
& Suppression
Oxygen Generation
CO2 Removal
Potable Water Processing
Urine Recovery
Brine
Brine Product
Brine Water Recovery
Cabin Air
Waste Mgmt
Recovered H2O
TCCS
Vented Waste Gas
Atmosphere Monitors
Brine & Urine Sensors
CO2 Reduction
Particulate Monitor
Acoustic Monitor
Microbial Monitor
(Water & Surfaces)
High P O2
DOES NOT IMPLY SELECTION! PRE-DECISIONAL!
Ag Biocide
PT Urine
O2/N2 Control
Water Quality Monitors
Filtration & Heavy VOC Removal
Temp & Humidity Control

## Slide 5: Air Revitalization System (ARS)
Shuttle Cabin Fan
Motorized Valves
Shuttle Condensing Heat Exchanger (CHX)
Shuttle Water Separator
Trace Contaminant Removal System (TCRS)
LiOH Canisters (CO2 Scrubber)

## Slide 6: HESTIA - ARS

## Slide 7: Air Revitalization System
The ARS provided 4 main functions to the chamber:
  Cooling the air
    Condensing heat exchanger, chiller carts
  Removing humidity from the air
    Condensing heat exchanger
  Removing trace contaminants
    Trace Contaminant Removal System
      Charcoal filter
      Ambient Temperature Catalytic Oxidizer (ATCO) filter
  Scrubbing Carbon Dioxide
    Reactive Plastic Lithium Hydroxide canisters (RP LiOH)
My focus: the Condensing Heat Exchanger (CHX)

## Slide 8: Condensing Heat Exchanger Performance
CHX Function: provide cooling () which removes heat from air (
No for our test at steady state
Ideal Case:
Liquid side is straight-forward:
Air side more involved
  Latent heat (phase change – condensing)
  Sensible heat (changes in temperature)

## Slide 9: Methods of calculating Qair (Qout)
Heat Removed from Air (Q air) |  | 
Psychometric chart |  | Enthalpy values read from chart
Calculated Enthalpy |  | Calculate enthalpy value for every specific temperature
Experimental |  | Curve fit enthalpy from recorded data
Average Enthalpy |  | Average Enthalpy kept constant
Heat Removed from Air (Q air) |  | 
Psychometric chart |  | Enthalpy values read from chart
Calculated Enthalpy |  | Calculate enthalpy value for every specific temperature
Experimental |  | Curve fit enthalpy from recorded data
Average Enthalpy |  | Average Enthalpy kept constant

## Slide 10: Experimental Calculation method
Term | Definition | Unit
Term | Definition | Unit
All other terms available from experiment data
Sensible heat of water vapor
Vary with temperature, need formula
Sensible heat of dry air
Latent heat of vaporization (condensation)
Notes: Add hg to terms

## Slide 11: Phase I Test Points
Test Point | Chiller Set Point (°C) | Coolant Inlet T (°C) | TCRS Air Flow Rate Set Point (CFM) | TCRS Air Flow Rate (CFM) | LiOH Air Flow Rate Set Point (CFM) | LiOH Air Flow Rate (CFM) | Exercise Profile | Humidity Injection rate set point (mL/min)
1 | 2 | 2.1 | 10.6 | 12.1 | 10.6 | 12.6 | 4 normal | 4.71
2 | 10 | 9.4 | 10.6 | 11.8 | 10.6 | 11.4 | 4 normal | 4.71
3 | 15 | 14.3 | 10.6 | 10.4 | 10.6 | 10.0 | 4 normal | 4.71
4 | 2 | 1.9 | 21.2 | 20.2 | 21.2 | 23.3 | 4 normal | 4.71
5 | 10 | 9.8 | 21.2 | 22.7 | 21.2 | 20.9 | 4 normal | 4.71
6 | 15 | 14.4 | 21.2 | 21.5 | 21.2 | 20.8 | 4 normal | 4.71
7 | 2 | 2.5 | 10.6 | 13.3 | 10.6 | 11.3 | 3 rest, 1 exercise | 21.38 (peak)

## Slide 12: CHX Performance

## Slide 13: CHX Performance
Figure 7: ARS Test Point 7 Energy Balance
*Spike in Qcoolant and Q air due to decrease in chiller cart temperature from 15°C to 2°C
Chart: Test Point 7: Qcooling vs Qair

## Slide 14: Current Work
Perform post-test calibration, improve instrumentation for future tests
Run further tests to determine discrepancies between and
Characterize potential sources
  i.e. measure water storage capacity in separator for additional condensate
Tie in ARS and other subsystem data collection
Develop new CHX to “plug in” to HESTIA 20’ chamber

## Slide 15: CHX Technology Development Problem & Need
CHX are a critical function of closed-loop life support
  ~50% of reclaimed water on ISS is from CHX condensate (up to 4lbs/hr)
  Utilizes a hydrophilic coating to gather condensate
Three problems with current technology
  Current CHX’s must be dried out on a monthly basis to mitigate bio-growth
    Uses crew time and resources which may not be available on long duration spaceflight
    Increases volume and mass with dual core “swingbed” approach
  Coatings slough off with time, causing the CHX to lose its hydrophilicity
    Current ISS CHX’s must be uninstalled and regenerated on earth on a regular basis
  Current coatings react with contaminants which cause downstream impacts to water processing system
    Chemical reaction between contaminants and coatings which produce DMSD’s that are difficult to remove from water
    Currently on ISS, filters can remove compounds, but are degraded at an accelerated rate (replaced every ~6 months)
To enable long duration spaceflight and reduce upmass/downmass a more robust CHX is needed
Notes: Upmass/downmass (minimize crew time
Add info for

## Slide 16: Condensing Heat Exchangers
Developing options for future CHX solutions
  UNL
  Orbitec
  Oceaneering
  Other SBIRs?
Integrated ECLSS testing will be used to verify technology
Will replace shuttle CHX in chamber

## Slide 17: Current Partnership: UNL
Currently partnered with University of Nebraska-Lincoln (UNL)
Utilize a femtosecond laser to physically create a hydrophilic surface, thereby bypassing the need for a coating
Seedling project plan:
  Investigate the manufacturability of laser processed surfaces (i.e. brazing, bending, and machining)
  Identify the ideal pattern:
    Bio-resistant
    Hydrophilic
    Not effected by siloxanes
  Investigate a cleanable siloxane filter to be used upstream of CHX
Leveraging UNL’s work with the Nebraska Research Initiative to develop an antibacterial and antifouling metal surface for the medical industry
Laser processing of fins for brazing and flat sheets for microbial testing
Construction of a 4”x4” test coupon for testing
Fins Undergoing Laser Processing
SEM Images of Finned Surface
Notes: Current TRL

## Slide 18: Summary
HESTIA’s development as a beneficial integrated testbed is well underway
Phase I testing proved its capability and generated useful data, as well as brought groups together earlier in the design/integration process
The “plug and play” design allows HESTIA to continue expanding as technologies mature
The ARS has aided in the demonstration of the need for new CHX technology
Future CHX work is promising, and the 20’ chamber will verify CHX capabilities such as:
  Cooling air
  Removing humidity
  Gathering condensate for regeneration
  Manufacturability
There are several promising CHXs in development
Notes: Without reparability, the system should be robust (easy to fix or hard to break balance)

## Slide 19: Questions?