## Maintenance Plan
Asset Category | SHARP | LRP System | Maximo System | Life Safety | Freq | Freq Val | Basic Job Steps | Requirement | Comments | Primary Job Plan Masters
Access Control Station | FIRE | SEC | PSY | N | RTF | 0 |  |  |  | N/A
Aerosol | FIRE | FPS | PSY | N | A1 | 1 | Visual inspection Component functional check |  | New category for potassium aerosol systems such as STAT-X. | PSSX001A
Aerosol | FIRE | FPS | PSY | N | SA | 0.5 | Visual inspection Component functional check |  | New category for potassium aerosol systems such as STAT-X. | PSSX001SA
AHU-CHW-5T_30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & replace filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 180 |  | HVAC20xxM4
AHU-CHW-5T_30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 180 |  | HVAC20xxA
AHU-CHW-Computer-5T_30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 181 |  | HVAC28xxM4
AHU-CHW-Computer-5T_30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 182 |  | HVAC28xxA
AHU-CHW-FCU | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
AHU-CHW-FCU-Special | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & replace filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 182 |  | N/A
AHU-CHW-GT30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 183 |  | N/A
AHU-CHW-GT30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 184 |  | N/A
AHU-CHW-LT5T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 185 | Additional FMC assets in Asset Category are in CIF M6-0342 an no longer maintained. | N/A
AHU-CHW-LT5T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 186 | Additional FMC assets in Asset Category are in CIF M6-0342 an no longer maintained. | N/A
AHU-CHW-M/U | HVAC | HVC | HVC | N | M2 | 0.16667 | Remove & Replace Filters. | Engineering analysis | Additional filter servicing requirement for outdoor air units. | N/A
AHU-CHW-M/U | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 185 | Additional FMC assets in Asset Category are in CIF M6-0342 an no longer maintained. | N/A
AHU-CHW-M/U | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 186 | Additional FMC assets in Asset Category are in CIF M6-0342 an no longer maintained. | N/A
AHU-DX | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 187 |  | N/A
AHU-DX | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 188 |  | N/A
AHU-DX-5T_30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 189 |  | N/A
AHU-DX-5T_30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 190 |  | N/A
AHU-DX-Computer-5T_30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. | Manufacturer’s recommendation. ASHRAE 62 & 191 |  | N/A
AHU-DX-Computer-5T_30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 192 |  | N/A
AHU-DX-Condenser | HVAC | HVC | HVC | N | A1 | 1 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. Visually check refrigerant and oil sight glasses (add if required) Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 193 | Approx. 18 assets have PMs performed at a higher (M4 & SA) frequency. | N/A
AHU-DX-GT30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser panVerify no leaks. Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge)Verify unit operational. Visually check refrigerant and oil sight glasses (add if required) | Manufacturer’s recommendation. ASHRAE 62 & 194 |  | N/A
AHU-DX-GT30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 195 |  | N/A
AHU-DX-LT5T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. Visually check refrigerant and oil sight glasses (add if required) | Manufacturer’s recommendation. ASHRAE 62 & 196 |  | N/A
AHU-DX-LT5T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 197 |  | N/A
AHU-DX-Package-5T_30T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. Visually check refrigerant and oil sight glasses (add if required) | Manufacturer’s recommendation. ASHRAE 62 & 198 |  | N/A
AHU-DX-Package-5T_30T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 199 |  | N/A
AHU-DX-Package-LT5T | HVAC | HVC | HVC | N | M4 | 0.33 | Remove and Replace Filters Remove & Replace Filters. Drain, condenser pan, and overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify delta temps (refrigerant charge) Verify unit operational. Visually check refrigerant and oil sight glasses (add if required) | Manufacturer’s recommendation. ASHRAE 62 & 200 |  | N/A
AHU-DX-Package-LT5T | HVAC | HVC | HVC | N | A1 | 1 | Same as M4 Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Manufacturer’s recommendation. ASHRAE 62 & 201 |  | N/A
AHU-DX-Package-Portable | HVAC | HVC | HVC | N | RTF | 0 |  |  |  | N/A
AHU-DX-Wall | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
AHU-DX-Window | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Air Receiver-Local | HVAC | HVC | HVC | N | PMHL | 0 | Verify condensate drain functional/Inspect for corrosion/Inspect Safety Relief valves/Verify properly tagged | Manufacturer’s recommendation. ASHRAE 62 & 201 | Local Air Receivers are in vicinity of Air Compressor that receives scheduled maintenance. Job Plan for Air Compressor includes tasks directed to these receivers. | N/A
Air Receiver-Remote | HVAC | HVC | HVC | N | A1 | 1 | Verify condensate drain functional/Inspect for corrosion/Inspect Safety Relief valves/Verify properly tagged | Manufacturer’s recommendation. ASHRAE 62 & 201 | Remote Air Receivers are distant from the facility's Air Compressor or is fed from one of the Plant compressed air loops. | N/A
Air Release Valve-Wastewater | WATER | WTR | WWS | N | A1 | 1 | Activate air release valve to clear air from system | Manufacturer recommended maintenance |  | N/A
Air Release Valve-Water | WATER | WTR | WWS | N | RTF | 0 |  |  |  | N/A
Air Separator | HVAC | HVC | HVC | N | RTF | 0 | Operational Check | Engineering analysis |  | N/A
Air Shower-Cleanroom | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Air Vent System | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Analyzer | MV | EHV | EHV | N | TBD | TBD |  |  | All Assets in PM/PEND status at time of publication | N/A
Analyzer-Drinking Water | WATER | WTR | WWS | N | RTF | 0 |  |  | Added per Water SHARP Team request 10/9/14. | N/A
ASSD | FIRE | FPS | PSY | Y | A1 | 1 | Visual inspection Component functional check | NFPA Life Safety - NFPA 101 designation by Fire Systems SHARP Team. | Air Sampling Smoke Detector Individual units (22) in LCC K6-0900 and (9) in O&C M7-0355 and (2) units in K6-1193 are PMHL are PMHL | N/A
ATS | LV | ELV | ELV | N | A2 | 2 | Functional test Visual inspection | NFPA 70B | Some ATS changed to mintenance code of MBU. Asset will have a PM executed prior to each use. Job Plan PLE022 will be used. | N/A
ATS-C5/Orsino | LV | ELV | ELV | N | A1 | 1 | Functional test Visual inspection | NFPA 70B | These ATSs are for the Station Service Transformers (provide control power to Circuit Breakers) in C5 and Orsino | N/A
ATS-Special | LV | ELV | ELV | Y | M1 | 0.08 | Functional test | NFPA 110 and 101 Life Safety - NFPA 101 designation by Fire Systems SHARP Team |  | N/A
ATS-Special | LV | ELV | ELV | Y | A1 | 1 | Functional test | IEEE 241 NFPA 110 and 101 Life Safety - NFPA 101 designation by Fire Systems SHARP Team |  | N/A
ATS-Static Special | LV | ELV | ELV | N | A1 | 1 | Functional test Visual inspection | NFPA 70B | MAR S0521 added this asset category 8/1/14. These are special transfer switches associated with the UPS system and the first of their kind. | N/A
Automatic Flush Station | WATER | WTR | WWS | N | RTF | 0 |  |  | All Assets are RTF status at time of publication | N/A
Backhoe | CIVIL | HEQ | FMT | N | SA | 0.5 | Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Battery Bank-Lead Acid (VRLA) | LV | ELV | ELV | N | SA | 0.5 | Perform predictive testing Visual inspection | NFPA 70B, 20. 17 NETA MTS | Consolidated from Battery Band-Lead Acid and Battery Bank-Valve Reguklated Lead Acid categories | N/A
Battery Bank-Nickel Cad | LV | ELV | ELV | N | SA | 0.5 | Perform predictive testing Visual inspection | NFPA 70B, 20.17 NETA MTS |  | N/A
Battery Charger | LV | ELV | ELV | N | A1 | 1 | Functional test Visual inspection Clean/vacuum area and equipment | NFPA 70B, 20.17 |  | N/A
Battery Charger-NM | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | N/A
Battery-Controls | CONTROLS | CTL | ELV | N | SA | 0.5 | Visual Inspection | Engineering analysis | PMs for this Asset Category are not sequenced. | N/A
Battery-Controls | CONTROLS | CTL | ELV | N | A1 | 1 | Functional Test | Engineering analysis | PMs for this Asset Category are not sequenced. | N/A
Battery-Fire-Controls | FIRE | CTL | PSY WWS | N | SA | 0.5 | Visual inspection Component functional check | Battery Load Test per NFPA 72, Table 14.4. 5 | PM included in monthly engine maintenance. Assets will typically be PMHL. | N/A
Battery-Fire-Engine | FIRE | FPS | WWS | N | M1 | 0.08 | Visual inspection Component functional check | Battery Load Test per NFPA 25, Table 8.1.2 | Includes monthly Controls PM. | N/A
Beam Detectors | FIRE | SEC | PSY | N | SA | 0.5 | Functional test Visual inspection | NFPA |  | N/A
BFP | WATER | WTR | WWS | N | A1 | 1 | Component functional check | FAC Chapter 62-555 |  | N/A
BFP-Fire | WATER | WTR | WWS | N | Q1 | 0.25 | Visual inspection | NFPA 25, chapter 13 | Negotiations with the AHJ resulted in Quarterly inspections as opposed to monthly recommended by NFPA for fire system BFPs | N/A
BFP-Fire | WATER | WTR | WWS | N | A1 | 1 | Same as Q Component functional check | FAC Chapter 62-555 | BFPs require annual testing per NFPA and FAC | N/A
BFP-Temp | WATER | WTR | WWS | N | RTF | 0 | Tested prior to use in temporary application | Engineering analysis |  | N/A
Blower | WATER | WST | WWS | N | SA | 0.5 | Rotating unit requires maintenance of fluids, couplings and air filter | Manufacturer’s recommendation |  | N/A
Blower | WATER | WST | WWS | N | A1 | 1 | Same as SA Change oil. Inspect, lubricate and clean electric motor. | Manufacturer’s recommendation |  | N/A
Blower-Portable | WATER | WST | WWS | N | RTF | 0 | N/A | Engineering analysis | These are portable gas fed blowers for Roads & Grounds department. Not in W&W failure class. | N/A
Boat | CIVIL | HEQ | FMT | N | SA | 0.5 | Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Boat- Work Platform | CIVIL | HEQ | FMT | N | MBU | 0 |  |  | Maintain Before Use | N/A
Boat-Air | CIVIL | HEQ | FMT | N | Q1 | 0.25 | Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Boat-Motor-Outboard | CIVIL | HEQ | FMT | N | SA | 0.5 | Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Boilers-Electric | HVAC | HVC | HVC | N | SA | 0.5 | Verify no water leaks. Raise water temp and verify operation of electrical components. Drain boiler and clean sludge, Check gauges and valves. Fill with water and verify operating properly. | Manufacturer’s recommendation |  | N/A
Boilers-HTHW | HVAC | HVC | HVC | N | A1 | 1 | Internal and external inspection. Clean fire side of tubes of soot buildup and corrosion. Replace safety valves with new or certified rebuilt safety valves. | Manufacturer’s recommendation. ASME B31.9 | Utility Annex Boilers only existing HTHW system. | N/A
Boilers-HTHW | HVAC | HVC | HVC | N | A1 | 1 | Inspect motor and starter. | Engineering analysis |  | N/A
Boilers-HTHW | HVAC | HVC | HVC | N | A1 | 1 | Verify calibration of transmitters and displays. | Engineering analysis |  | N/A
Boilers-HW | HVAC | HVC | HVC | N | SA | 0.5 | Verify igniter, reed valve, NG valve, condenser water are operating nominally Verify no water or gas leaks | Manufacturer’s recommendation | Split HW/ Steam and Modulating/Pulse- nozzles, electrodes and pump | N/A
Boilers-HW | HVAC | HVC | HVC | N | A1 | 1 | Same as A | Manufacturer’s recommendation | Split HW/ Steam and Modulating/Pulse- nozzles, electrodes and pump | N/A
Boilers-Modular/Pulse | HVAC | HVC | HVC | N | SA | 0.5 | Verify igniter, reed valve, NG valve, condenser water are operating nominally Verify no water or gas leaks | Manufacturer’s recommendation | Split HW/ Steam and Modulating/ Pulse | N/A
Boilers-Modular/Pulse | HVAC | HVC | HVC | N | A1 | 1 | Same as SA | Manufacturer’s recommendation | Split HW/ Steam and Modulating/ Pulse | N/A
Boilers-Portable | HVAC | HVC | HVC | N | MBU | 0 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect safety valves and other components. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Replace safety valves. |  | 10/9/14 HVAC SHARP Team changed maintenance to be performed before first use. Job plan HBVH05A will be used. | N/A
Boiler-Steam-M7-0411 | HVAC | HVC | HVC | N | A1 | 1 |  |  |  | N/A
Boiler-Steam-M7-0411 | HVAC | HVC | HVC | N | Q1 | 0.25 |  |  |  | N/A
Bridge-Cabinet-I/O | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Cabinet-Terminal | STRUCTURAL | BRG | MEC | N | A4 | 4 | Megger conductors Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Collect and record asset data. Perform housekeeping activities. | Florida DOT |  | N/A
Bridge-Cable-Submarine | STRUCTURAL | BRG | MEC | N | A4 | 4 | Megger conductors Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Collect and record asset data. Perform housekeeping activities. | Florida DOT |  | N/A
Bridge-Control | CONTROLS | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Dynamic Braking | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Fender | STRUCTURAL | BRG | MEC | N | A1 | 1 | Inspect all wooden elements of fender system | Florida DOT |  | N/A
Bridge-Gates | STRUCTURAL | BRG | MEC | N | SA | 0.5 | Lubricate all movable parts Verify proper oil levels Perform operational test | Florida DOT |  | N/A
Bridge-Gates | STRUCTURAL | BRG | MEC | N | A1 | 1 | Same as SA Electrical check-out | Florida DOT |  | N/A
Bridge-Horn | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Light-Special | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Lock Bar | STRUCTURAL | BRG | MEC | N | Q1 | 0.25 | Lubricate all movable parts Verify proper oil levels Perform operational test | Florida DOT |  | N/A
Bridge-Lock Bar | STRUCTURAL | BRG | MEC | N | SA | 0.5 | Same as Q | Florida DOT |  | N/A
Bridge-MCC | STRUCTURAL | BRG | STR | N | A2 | 2 | Visual Inspection of enclosure and operating Mechanisms Verify properly labeled Thermal scan connections Clean enclosure Insulation test for MCC bus Operate bucket circuit breakers | Engineering analysis | PM scheduled times to be 4 hours per PM x 2 Person | N/A
Bridge-Motor-Span Lift | STRUCTURAL | BRG | MEC | N | A1 | 1 | Megger conductors Conduct Ohmic testing Verify proper operation of span motors Perform operational test | Florida DOT |  | N/A
Bridge-Nav Horn | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Remote Opr Station | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Scanner System | STRUCTURAL | BRG | MEC | N | RTF | 0 | Operational Check | Engineering analysis |  | N/A
Bridge-Span Lift | STRUCTURAL | BRG | MEC | N | M2 | 0.16667 | Megger conductors Conduct ohmic testing Verify proper operation of span motors Perform operational test | Florida DOT |  | N/A
Bridge-Structure | STRUCTURAL | BRG | MEC | N | M2 | 0.16667 | Structural Inspection | USCG Regulation | Two documented assets at time of publishing. | N/A
Bridge-Thruster Brake | STRUCTURAL | BRG | MEC | N | A1 | 1 | Lubricate all movable parts Verify proper oil levels Perform operational test Motor: Megger conductors Conduct ohmic testing Verify proper operation of span brake motors Perform operational test | Florida DOT |  | N/A
Bridge-Traffic | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Traffic Gong | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Bridge-Traffic Light | STRUCTURAL | BRG | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Brush Cut | CIVIL | HEQ | FMT | N | SA | 0.5 | Inspect (visually or otherwise) to assess condition Perform lubrication activities Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Bus-LV | LV | ELV | ELV | N | A4 | 4 | Insulation Resistance test Infrared scan Visual inspection Clean & vacuum enclosure (inside & outside) | NFPA70B, 24.5.2.2 | 5/19/14-SHARP Team. Maint Code changed from PM to PMHL. Will be maintained at the higher level Substation PM. | N/A
Bus-MV | MV | EHV | EHV | N | A2 | 2 | Visual inspection IR Scan Hi pot test Clean & vacuum enclosure (inside & outside) | NFPA70B 24.5.2.1 |  | N/A
Bus-MV | MV | EHV | EHV | N | A4 | 4 | Visual inspection IR Scan Hi pot test Clean & vacuum enclosure (inside & outside) | NFPA70B 24.5.2.2 | Exceptions to A4 are for Bus in switchgear | N/A
BWC | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Cable-Aerial | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Cable-Underground | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Car-Electric | CIVIL | HEQ | FMT | N | SA | 0.5 | Inspect (visually or otherwise) to assess condition Perform lubrication activities Collect and record asset data | Manufacturer’s recommendation |  | N/A
Carousel | N/A | N/A | MEC | N | RTF | 0 |  | Engineering analysis |  | N/A
Cart | CIVIL | HEQ | FMT | N | SA | 0.5 |  |  |  | N/A
Cart-4 Wheeler | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | N/A
Cart-Golf | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Engineering analysis |  | N/A
Cart-Golf Electric | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Engineering analysis |  | N/A
Cart-Golf Gas | CIVIL | HEQ | FMT | N | RTF | 0 | Run to failure/ equipment will be checked out when brought in for repair | Engineering analysis |  | N/A
Cathodic Prot | LV | OPS | ELV | N | SA | 0.5 | Take measurement Visual inspection Clean & vacuum enclosure (inside & outside) | NFPA 70B | Tthe VAB Roof (A) and Water Tanks (SA) | N/A
CFMS | FIRE | FPS | PSY | N | A1 | 1 |  |  |  | N/A
Channel Markers | STRUCTURAL | STR | RDG | N | RTF | 0 | Visual Inspection by watercraft (Is signage intact or damaged or missing) (Is pile leaning) (Cardinal direction that signage faces) | Customer Request |  | N/A
Charger Analyzer | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Chiller | HVAC | HVC | HVC | N | A1 | 1 | Verify refrigerant charge by comparing the evaporator saturation temperature and the CHW leaving temperature (+/- 1 degree) Verify unit is operating nominally Verify refrigerant charge via electronic wand for all seals and fittings | Manufacturer’s recommendation |  | N/A
Chiller | HVAC | HVC | HVC | N | Q1 | 0.25 | Verify refrigerant charge by comparing the evaporator saturation temperature and the CHW leaving temperature (+/- 1 degree) Verify unit is operating nominally Verify refrigerant charge via electronic wand for all seals and fittings | Manufacturer’s recommendation |  | N/A
Chiller | HVAC | HVC | HVC | N | SA | 0.5 | Verify refrigerant charge by comparing the evaporator saturation temperature and the CHW leaving temperature (+/- 1 degree) Verify unit is operating nominally Verify refrigerant charge via electronic wand for all seals and fittings | Manufacturer’s recommendation |  | N/A
Chiller | HVAC | HVC | HVC | N | M30 | 2.5 |  | Manufacturer’s recommendation |  | N/A
Chiller-Backup | HVAC | HVC | HVC | N | SA | 0.5 | Verify refrigerant charge by comparing the evaporator saturation temperature and the CHW leaving temperature (+/- 1 degree) Verify unit is operating nominally Verify refrigerant charge via electronic wand for all seals and fittings | Manufacturer’s recommendation |  | N/A
Chiller-Backup | HVAC | HVC | HVC | N | M1 | 0.08 | Verify proper backup support of chiller to facility. | Facility user’s recommendation |  | N/A
Chiller-Compressor-Remote | HVAC | HVC | HVC | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
Chiller-Compressor-Remote | HVAC | HVC | HVC | N | A2 | 2 |  | Manufacturer’s recommendation |  | N/A
Chiller-GT300T | HVAC | HVC | HVC | N | Q1 | 0.25 | Verify refrigerant charge via electronic wand for all seals and fittings Collect ferrographic and/or IR data | Manufacturer’s recommendation |  | N/A
Chiller-GT300T | HVAC | HVC | HVC | N | Q1 | 0.25 | Perform data collection at the appropriate locations on the equipment per the data collector. | Engineering analysis |  | N/A
Chiller-GT300T | HVAC | HVC | HVC | N | SA | 0.5 | Same as Q Verify refrigerant charge via electronic wand for all seals and fittings Collect ferrographic and/or IR data | Manufacturer’s recommendation |  | N/A
Chiller-GT300T | HVAC | HVC | HVC | N | SA | 0.5 | Perform oil sample collection at the appropriate locations on the equipment. | Engineering analysis |  | N/A
Chiller-GT300T | HVAC | HVC | HVC | N | A1 | 1 | Same as SA Verify refrigerant charge via electronic wand for all seals and fittings | Manufacturer’s recommendation |  | N/A
Chiller-GT300T | HVAC | HVC | HVC | N | M30 | 2.5 | Same as A. Verify refrigerant charge via electronic wand for all seals and fittings Clean Condenser tubes | Manufacturer’s recommendation |  | N/A
Chiller-Package | HVAC | HVC | HVC | N | SA | 0.5 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Chiller-Portable | HVAC | HVC | HVC | N | A1 | 1 | Verify refrigerant charge Verify unit is operating nominally Perform housekeeping | Engineering analysis | Verify proper operation of chiller prior to start of each hurricane season. | N/A
Chiller-Portable GE 100T | HVAC | HVC | HVC | N | A1 | 1 |  | Manufacturer’s recommendation |  | N/A
Circuit Breaker-ACB | LV | ELV | ELV | N | A4 | 4 | Functional test Infrared scan Visual inspection Clean & vacuum inside and outside the enclosure. | Engineering analysis |  | N/A
Circuit Breaker-Insulated | LV | ELV | ELV | N | RTF | 0 | Functional test Infrared scan Visual inspection Clean & vacuum inside and outside the enclosure. | NETA MTS and Engineering analysis | PM will be performed as part of the Press site Generator PM procedure. Maint code PMHL. | N/A
Circuit Breaker-LV Draw Out | LV | ELV | ELV | N | A4 | 4 | Functional Test Cleaning Lubrication Visual inspection | NETA MTS and Engineering analysis | 5/19/14 LV SHARP Team assets reassigned from Circuit Breaker-Draw Out. Asset maintenance code will be PMHL and will be maintained at the higher level Substation PM. | N/A
Circuit Breaker-Molded Case | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Circuit Breaker-MV-Draw Out | MV | EHV | EHV | N | A2 | 2 |  | Engineering analysis | Assets reassigned from Circuit Breaker-Draw Out. Asset maintenance code will be PMHL and will be maintained at the higher level Substation PM. | N/A
Circuit Breaker-SF6 | MV | EHV | EHV | N | A2 | 2 | Functional test PF Test Visual inspection. Trip test if equipped with trip unit. Clean & vacuum inside and outside the enclosure. Verify Grounding Clean Insulators Withstand Test Resistance Test | NFPA 70B, NETA MTS and Engineering RCM analysis | All assets are located at Orsino (M6-0996) and at C5 (K6-1145) | PLTB19xxA4
Circuit Breaker-VCB | MV | EHV | EHV | N | A4 | 4 | Functional test Visual inspection. Trip test if equipped with trip unit Clean & vacuum inside and outside the enclosure. | Engineering analysis | 43 assets are maintained at A1 (3) and A2 (40) frequencies. | N/A
Circuit Breaker-VCB-C5/Orsino | MV | EHV | EHV | N | A2 | 2 | Functional test Visual inspection. Trip test if equipped with trip unit. Clean & vacuum inside and outside the enclosure. | Engineering analysis |  | N/A
Clock | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
CO2 | FIRE | FPS | PSY | N | A1 | 1 | Comply with Code requirements. Collect and record asset data. | NFPA |  | PSC001xxxA
Come Along | CIVIL | HEQ | FMT | N | A1 | 1 | Load Test | NASA 8719.9 |  | HEM125A
Compactor-Landfill | CIVIL | HEQ | FMT | N | A1 | 1 | Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | HEM073A
Compartment | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Compressor-Refrigerant | HVAC | HVC | HVC | N | SA | 0.5 |  | Manufacturer’s recommendation
Compressors-Air-Portable | HVAC | AIR | FMT HVC | N | RTF | 0 |  | Engineering analysis | Generally less than 5 hp. May have PMs assigned if above 5 hp or based on operating context. Some assets with tanks may have SPCC inspections. 4 portable air compressors HE905092, HE905140, J8ACACP001, J8ACACP002 changed to MBU | HETANKxxM1
Compressors-Air-Portable-Large Eng | HVAC | AIR | FMT | N | A2 | 1 |  | Engineering analysis |  | HEMXXXA
Compressors-Air-Portable-MBU | HVAC | AIR | FMT HVC | N | MBU | 0 |  | Engineering analysis | 4 portable air compressors HE905092, HE905140, J8ACACP001, J8ACACP002 changed to MBU | HVCA02MBU
Compressors-Air-Portable-Small Eng | HVAC | AIR | HVC | N | SA | 0.5 |  | Manufacturer’s recommendation |  | HEMXXXSA
Compressors-Air-Reciprocating | HVAC | AIR | HVC | N | M4 | 0.33 | Check oil Check belts Check for leaks using ultrasonic gun Change air separator & oil filters Verify condensate valve is operating Thermal scan Vibration data collection Verify unit is operating nominally | Manufacturer’s recommendation | Some assets may have M1 SPCC tank inspections. Additionally, 13 have SA frequencies. Compressed Air SHARP Team dissolved and Asset Categories moved to HVAC. | HVCA01xxM4
Compressors-Air-Reciprocating | HVAC | AIR | HVC | N | A1 | 1 | Same as M4 Change Oil | Manufacturer’s recommendation |  | HVCA01xxxA
Compressors-Air-Recip-w/Drum | HVAC | AIR | HVC | N | M4 | 0.33 | Check oil Check belts Check for leaks using ultrasonic gun Change air separator & oil filters Verify condensate valve is operating Thermal scan Vibration data collection Verify unit is operating nominally | Manufacturer’s recommendation |  | HVCA01xxM4
Compressors-Air-Recip-w/Drum | HVAC | AIR | HVC | N | A1 | 1 | Same as M4 Change Oil | Manufacturer’s recommendation |  | HVCA01xxM4
Compressors-Air-Recip-w/Drum | HVAC | AIR | HVC | N | M1 | 0.083 |  | Operational Check | Monthly condensate container check | HVCAXXM
Compressors-Air-Recip-w/Drum | HVAC | AIR | HVC | N | A1 | 1 | Same as M4 Change Oil | Manufacturer’s recommendation |  | HVCA01xxA1
Compressors-Air-Screw | HVAC | AIR | HVC | N | M4 | 0.33 | For UA, IACP & Corrosion Control compressors: Check oil Check belts Check for leaks using ultrasonic gun Change air separator & oil filters Verify condensate valve is operating Thermal scan Vibration data collection Verify unit is operating nominally | Manufacturer’s recommendation |  | HVCA02xxM4
Compressors-Air-Screw | HVAC | AIR | HVC | N | A1 | 1 | Same as M4 Check/change cooler hoses | Manufacturer’s recommendation | Other requirements include separate Job Plans for subcomponents. Compressed Air SHARP Team dissolved and Asset Categories moved to HVAC. | HVCA02xxxA
Compressors-Air-Screw-SPCC | HVAC | AIR | HVC | N | M4 | 0.33 | For UA, IACP & Corrosion Control compressors: Check oil Check belts Check for leaks using ultrasonic gun Change air separator & oil filters Verify condensate valve is operating Thermal scan Vibration data collection Verify unit is operating nominally | Manufacturer’s recommendation |  | HVCA02xxM4
Compressors-Air-Screw-SPCC | HVAC | AIR | HVC | N | A1 | 1 | Same as M4 Check/change cooler hoses | Manufacturer’s recommendation | Other requirements include separate Job Plans for subcomponents. Compressed Air SHARP Team dissolved and Asset Categories moved to HVAC. | HVCA02xxxA
Compressors-Air-Screw-SPCC | HVAC | AIR | HVC | N | A1 | 1 | Inspect oil-filled reservoirs, piping for leaks. Inspect secondary containment. | Regulatory compliance. | The scope of this job plan is to visually inspect inventory locations which potentially store petroleum products in storage tanks or containers holding 55 gallons or more. | HVPROC01xxA1
Compressors-Air-Screw-w/Drum | HVAC | AIR | HVC | N | M4 | 0.33 | For UA, IACP & Corrosion Control compressors: Check oil Check belts Check for leaks using ultrasonic gun Change air separator & oil filters Verify condensate valve is operating Thermal scan Vibration data collection Verify unit is operating nominally | Manufacturer’s recommendation |  | HVCA02xxM4
Compressors-Air-Screw-w/Drum | HVAC | AIR | HVC | N | A1 | 1 | Same as M4 Check/change cooler hoses | Manufacturer’s recommendation | Other requirements include separate Job Plans for subcomponents. Compressed Air SHARP Team dissolved and Asset Categories moved to HVAC. | HVCA02xxxA
Compressors-Air-Screw-w/Drum | HVAC | AIR | HVC | N | M1 | 0.083 |  | Operational Check | Monthly condensate container check | HVCAXXM
Compressors-Air-System | HVAC | AIR | HVC | N | RTF | 0 |  | Engineering analysis | Assigned assets are compressed air systems and piping. Compressed Air SHARP Team dissolved and Asset Categories moved to HVAC. | N/A
Compressors-CNG | HVAC | HVC | HVC | N | Q1 | 0.25 | Check oil level Check belts Check for leaks using ultrasonic gun Vibration data collection Housekeeping IR scan Verify unit is operating nominally | Manufacturer’s recommendation | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Compressors-CNG | HVAC | HVC | HVC | N | A1 | 1 | Same as Q. Change air separator & oil filters Verify condensate valve is operating | Manufacturer’s recommendation | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Compressors-CNG | HVAC | HVC | HVC | N | A3 | 3 | Same as A. Perform functional test of PRDs/Affix operational check label | Manufacturer’s recommendation | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Condensing Unit | HVAC | HVC | HVC | N | M4 | 0.33 | Verify unit is operating nominally Verify delta temperatures (refrigerant charge) Clean coils | Manufacturer’s recommendation |  | N/A
Condensing Unit | HVAC | HVC | HVC | N | A1 | 1 | Verify unit is operating nominally Verify delta temperatures (refrigerant charge) Clean coils | Manufacturer’s recommendation |  | N/A
Condensing Unit-Piping | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Contactor | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Control Cubicle | CONTROLS | CTL | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Controller | CONTROLS | CTL | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Controls | CONTROLS | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Controls-BAS | CONTROLS | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Controls-CBM | CONTROLS | CTL | ELV | N | RTF | 0 |  | Engineering analysis | Condition Based Montioring Asset Type - INST | N/A
Controls-Chlorinator | CONTROLS | CTL | WWS | N | RTF | 0 |  | Engineering analysis | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Controls-Fire | FIRE | CTL | PSY WWS | Y | A1 | 1 | Component functional check | NFPA 72, Table 14 .4.5 Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Controls-Fire-Pump | FIRE | CTL | PSY WWS | Y | A1 | 1 | Component functional test | Testing per NFPA 25, paragraph 8.3.3. 5 Life Safety - NFPA 101 designation by Fire Systems SHARP Team. | Monthly is requirement now in the Battery-Fire-Engine requirement. Controls SHARP Team dissolved, Asset Category moved to this SHARP Team. | N/A
Controls-Gateway | CONTROLS | CTL | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Controls-Plant | HVAC | CTL | ELV | N | RTF | 0 |  |  |  | N/A
Controls-PLC | CONTROLS | CTL | ELV | N | RTF | 0 |  | Engineering analysis | Assets that provide a battery status indicator to a remote monitoring station or use non-volatile memory to store the source code do not require a PM. | N/A
Controls-PLC-Battery | CONTROLS | CTL | ELV | N | A4 | 4 | Replace battery | Engineering analysis | Assigned assets are associated with PAPI lights and not being used therefore are RTF. | N/A
Controls-Server | CONTROLS | CTL | ELV | N | Q1 | 0.25 | OS Security Patches | NASA IT Security Requirement | PMs currently performed via FootPrint, not in Maximo | N/A
Controls-Sound Suppression | CONTROLS | CTL | WWS | N | RTF | 0 | Component functional check | Engineering analysis |  | N/A
Controls-Workstation | CONTROLS | CTL | ELV | N | Q1 | 0.25 | OS Security Patches | NASA IT Security Requirement | PMs currently performed via FootPrint, not in Maximo | N/A
Conveyor | N/A | N/A | SPE | N | RTF | 0 |  | Engineering analysis | Primarily in warehouses | N/A
Cooling Tower | HVAC | HVC | HVC | N | Q1 | 0.25 | Verify condenser water, fans, and pumps are operating nominally Add gear box oil | Manufacturer’s recommendation | There are multiple asset configurations in this Category with varying degrees of maintenance required. | N/A
Cooling Tower | HVAC | HVC | HVC | N | SA | 0.5 | Verify condenser water, fans, and pumps are operating nominally Add gear box oil Collect ferrographic and/or IR data | Manufacturer’s recommendation | There are multiple asset configurations in this Category with varying degrees of maintenance required. | N/A
Cooling Tower | HVAC | HVC | HVC | N | A1 | 1 | Same as SA Deservice & clean basin | Manufacturer’s recommendation | There are multiple asset configurations in this Category with varying degrees of maintenance required. | N/A
Cooling Tower (Plant) | HVAC | HVC | HVC | N | Q1 | 0.25 | Verify condenser water, fans, and pumps are operating nominally | Engineering Analysis |  | N/A
Cooling Tower (Plant) | HVAC | HVC | HVC | N | Q1 | 0.25 | Perform data collection at the appropriate locations on the equipment per the data collector. | Engineering analysis |  | N/A
Cooling Tower (Plant) | HVAC | HVC | HVC | N | SA | 0.5 | Same as Q Add gear box oil Collect ferrographic and/or IR data | Engineering Analysis |  | N/A
Cooling Tower (Plant) | HVAC | HVC | HVC | N | SA | 0.5 | Perform oil sample collection at the appropriate locations on the equipment. | Engineering analysis |  | N/A
Cooling Tower (Plant) | HVAC | HVC | HVC | N | A1 | 1 | Same as SA Deservice & clean basin | Engineering Analysis |  | N/A
Cooling Tower (Plant) | HVAC | HVC | HVC | N | A1 | 1 | Inspect motor and starter. | Engineering analysis |  | N/A
Cooling Tower-BFF | HVAC | HVC | HVC | N | SA | 0.5 |  | Engineering Analysis |  | N/A
Counter-Particles | HVAC | HVC | HVC | N | PMHL | 0 | Remove device, install newly calibrated device, record asset # and calibration due date of replacement device | Engineering analysis | Particle counter asset will be maintained under a PM WON issued against the Location asset where the transmitter is in operation. | N/A
Counter-Particles-Portable | HVAC | HVC | HVC | N | PMHL | 0 | Remove device, install newly calibrated device, record asset # and calibration due date of replacement device | Engineering analysis | Particle counter asset will be maintained under a PM WON issued against the Location asset where the transmitter is in operation. | N/A
Crane | CIVIL | HEQ | FMT | N | M1 | 0.08 | Check and maintain fluid levels Inspect (visually or otherwise) to assess condition Collect and record asset data | Manufacturer’s recommendation | There are multiple asset configurations in this Category with varying degrees of maintenance required. | N/A
Crane | CIVIL | HEQ | FMT | N | SA | 0.5 | Load test Inspection | ANSI | There are multiple asset configurations in this Category with varying degrees of maintenance required. | N/A
Crane-Floor | EC&D | CRN | MEC | N | A1 | 1 | Load test | NASA 8719.9 | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
CRMS | FIRE | FPS | PSY | Y | A1 | 1 | Visual inspection | NFPA Life Safety - NFPA 101 designation by Fire Systems SHARP Team |  | N/A
Culverts | CIVIL | STM | RDG | N | TBD | TBD | No regularly scheduled inspections. Projects generated via SE, Environmental, customer requests or RTC. | Engineering analysis | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Cutter-Rescue | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | N/A
Cutter-Tractor Mounted | CIVIL | HEQ | FMT | N | SA | 0.5 | Heavy Equipment Inspection Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Exercise and/or operate component(s) Inspect (visually or otherwise) to assess condition Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
CW System | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Cypher Lock | FIRE | SEC | PSY | N | RTF | 0 |  | Engineering analysis | Controls SHARP Team dissolved, Asset Category moved to this SHARP Team. | N/A
Damper-Motorized | HVAC | HVC | HVC | N | A1 | 1 | Verify proper operation of damper. |  |  | N/A
Dampers | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Datalogger | LV | ELV | ELV
Dehumidifier | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Desiccant-Air Dryer | HVAC | HVC | HVC | N | A1 | 1 | Verify condensate drain functional Verify shuttle valves operational Verify unit is operational | Manufacturer’s recommendation |  | N/A
Desiccant-Air Dryer-BFF | HVAC | HVC | HVC | N | A1 | 1 | Verify condensate drain functional Verify shuttle valves operational Verify unit is operational | Manufacturer’s recommendation |  | N/A
Desiccant-Air Dryer-With Sampling | HVAC | HVC | HVC | N | A1 | 1 |  | Manufacturer’s recommendation |  | N/A
Desiccant-Air Dryer-With Sampling | HVAC | HVC | HVC | N | M1 | 0.083 |  | Manufacturer’s recommendation |  | N/A
Disconnect Switch-LV | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Disconnect Switch-MV | MV | EHV | EHV | N | A5 | 5 | Functional test Lubricate Infrared scan Visual inspection Clean/vacuum enclosure (interior & exterior) | Manufacturer’s recommendation. |  | N/A
Dispenser-CNG | HVAC | HVC | HVC MEC | N | W1 | 0.02 | Inspect Perform operational test | Manufacturer’s recommendation |  | N/A
Distribution-Duct-Diffuser | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Dock Leveler | STRUCTURAL | STI | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Door Portal | FIRE | SEC | PSY | N | SA | 0.5 | Visual inspection Component functional check | NFPA | Controls SHARP Team dissolved, Asset Category moved to this SHARP Team. | PSES1xxxSA
Doors-Fire | EC&D | DOR | STR | N | A1 | 1 | Inspect Perform operational test | Engineering analysis |  | BSM127xxxA
Doors-Misc | EC&D | DOR | STR | N |  |  |  |  | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied
Doors-Ped | EC&D | DOR | STR | N | SA | 0.5 | Inspect Perform operational test | Engineering analysis |  | BSM130SA
Doors-Roll Up-Elec-BFF | EC&D | DOR | STR | N | A1 | 1 | Inspect Perform operational test | Engineering analysis | For BFF Roll Up Elec Doors | BSM046xxxA
Doors-Roll-up Elec | EC&D | DOR | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Doors-Roll-up Elec-Fire | EC&D | DOR | STR | N | A1 | 1 | Inspect Perform operational test | Engineering analysis | For the Fire Stations | BSM046xxxA BSM001xxxA BSM152xxxA
Doors-Roll-up Manual | EC&D | DOR | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Doors-Rollup Manual-Boeing | EC&D | DOR | STR | N | PM |  |  | Engineering Analysis | Asset AB502010 at K6-0894 will be an RTF | N/A
Doors-Sliding Electric | EC&D | DOR | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Doors-Swing Electric | EC&D | DOR | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Doors-Vertical-High Bay | EC&D | DOR | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Dozer | CIVIL | HEQ | FMT | N | SA | 0.5 | Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Drainage Ditches | CIVIL | STM | RDG | N | TBD | TBD | No regularly scheduled inspections. Projects generated via SME, customer requests or RTC | Engineering analysis | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Drum | N/A |  |  | N | M1 | 0.08 |  | Environmental | 55 gallon drums only | N/A
Drum Handling | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Exercise and/or operate component(s) Inspect (visually or otherwise) to assess condition Make adjustments as required Collect and record asset data | NASA 8719.9 |  | N/A
Drum-Less Than 55 Gal | N/A |  | TBD | N | RTF | 0 |  |  |  | N/A
Dry Chem | FIRE | FPS | PSY | N | SA | 0.5 | Functional test Visual inspection | NFPA | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Dry Hydrants | WATER | WTR | WWS | N | RTF |  | N/A | Engineering analysis |  | N/A
Dry Pipe | FIRE | FPS | PSY | N | A3 | 3 |  |  |  | N/A
Dry Pipe | FIRE | FPS | PSY | N | SA | 0.5 |  |  |  | N/A
Dust Collector | HVAC | HVC | HVC | N | SA | 0.5 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). | Manufacturer’s recommendation |  | N/A
Dust Collector | HVAC | HVC | HVC | N | A1 | 1 | Same as SA Check motor to turbine coupling | Manufacturer’s recommendation |  | N/A
Electric Door Latch | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Electric Heater | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Electrical Filter Assembly | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Electrical Misc | LV | ELV | ELV | N |  |  |  |  | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Elevator, Conveyor | EC&D | ELE | MEC | N | A1 | 1 | Inspection and Operational Check | ASME B20.1 - 2015 Safety Standard for Conveyors and Related Equipment |  | N/A
Elevator, Drum | EC&D | ELE | TBD | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation |  | N/A
Elevator, Hydraulic | EC&D | ELE | MEC | N | SA | 0.5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic | EC&D | ELE | MEC | N | M1 | 0.08 | Perform Fire service recall test | NFPA 70 and 72 |  | N/A
Elevator, Hydraulic | EC&D | ELE | MEC | N | A1 | 1 | QEI Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic, Air Force | EC&D | ELE | MEC | N | SA | 0.5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic, Air Force | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic, Air Force | EC&D | ELE | MEC | N | A1 | 1 | QEI Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic, Air Force | EC&D | ELE | MEC | N | M1 | 0.08 | Perform Fire service recall test | NFPA 70 and 72 |  | N/A
Elevator, Hydraulic, Material Lift | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Hydraulic, Material Lift | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Lift-Personnel | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Rack & Pinion | EC&D | ELE | MEC | N | A3 | 3 | Change machine gearsbox. | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Rack & Pinion | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Rack & Pinion | EC&D | ELE | MEC | N | M1 | 0.08 | Perform Fire service recall test | NFPA 70 and 72 |  | N/A
Elevator, Rack & Pinion | EC&D | ELE | MEC | N | Q1 | 0.25 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Rack & Pinion | EC&D | ELE | MEC | N | A1 | 1 | QEI Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Rack & Pinion | EC&D | ELE | MEC | N | M1 | 0.08 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction | EC&D | ELE | MEC | N | A5 | 5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction | EC&D | ELE | MEC | N | SA | 0.5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction | EC&D | ELE | MEC | N | M1 | 0.08 | Perform Fire service recall test | NFPA 70 and 72 |  | N/A
Elevator, Traction | EC&D | ELE | MEC | N | Q1 | 0.25 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction | EC&D | ELE | MEC | N | A1 | 1 | QEI Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, 500 WT | EC&D | ELE | MEC | N | SA | 0.5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, 500 WT | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, 500 WT | EC&D | ELE | MEC | N | A1 | 1 | QEI Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, 500 WT | EC&D | ELE | MEC | N | M1 | 0.08 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, 500 WT | EC&D | ELE | MEC | N | Q1 | 0.25 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, Gear | EC&D | ELE | MEC | N | A3 | 3 | Change machine gearsbox. | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, Gear | EC&D | ELE | MEC | N | A5 | 5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, Gear | EC&D | ELE | MEC | N | SA | 0.5 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, Gear | EC&D | ELE | MEC | N | A1 | 1 | Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Elevator, Traction, Gear | EC&D | ELE | MEC | N | M1 | 0.08 | Perform Fire service recall test | NFPA 70 and 72 |  | N/A
Elevator, Traction, Gear | EC&D | ELE | MEC | N | A1 | 1 | QEI Operational Check | ASME 17.1 & A17.2 ANSI / OSHA Manufacturer’s recommendation. |  | N/A
Emer Lights | LV | ELV | ELV | Y | M1 | 0.08 | Functional monthly test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Individual assets are indicated as PMHL. These are legacy fixtures. No self-testing and therefore require M and A PM’s to insure the battery/lamps meet requirements. | N/A
Emer Lights | LV | ELV | ELV | Y | A1 | 1 | Functional Annual test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Individual assets are indicated as PMHL. These are legacy fixtures. No self-testing and therefore require M and A PM’s to insure the battery/lamps meet requirements. | N/A
Emer Lights-Self Testing | LV | ELV | ELV | Y | A1 | 1 | Self testing monthly requirement. Functional Annual test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Individual assets are indicated as PMHL. Monthly self-testing | N/A
Emer Lights-Self Testing 2 | LV | ELV | ELV | Y | RTF | 0 | Completely self-diagnostic | NFPA-101 Life Safety designation by AHJ , SHARP Team. | These fixtures perform both the Monthly and Annual tests automatically. Manual PMs not required. | N/A
Emer Pwr Sys | MV | EHV | EHV | Y | M1 | 0.08 | Functional test Infrared scan Visual inspection Clean/Vacuum enclosure (interior & exterior) | Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Emer Pwr Sys | MV | EHV | EHV | Y | SA | 0.5 | Functional test Infrared scan Visual inspection Clean/Vacuum enclosure (interior & exterior) | Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Emer-Exit Lights | LV | ELV | ELV | Y | A1 | 1 | Functional Annual test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Assigned to one asset (ie "ELITE" or system level asset) and covers the entire facility both Emergency and Exit Lights. Each Individual light has a maint code of PMHL for the Lights maintained as referenced in EEL docs. | N/A
Emer-Exit Lights | LV | ELV | ELV | Y | M1 | 0.08 | Functional monthly test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Assigned to one asset (ie "ELITE" or system level asset) and covers the entire facility both Emergency and Exit Lights. Each Individual light has a maint code of PMHL for the Lights maintained as referenced in EEL docs. | N/A
Emer-Exit Lights Self Testing | LV | ELV | ELV | Y | A1 | 1 | Functional Annual test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Assigned to one asset (ie "ELITE" or system level asset) and covers the entire facility both Emergency and Exit Lights. Each Individual light has a maint code of PMHL for the Lights maintained as referenced in EEL docs. | N/A
Emer-Exit Lights Self Testing | LV | ELV | ELV | Y | A1 | 1 | Functional Annual test Visual inspection | NFPA-101 Life Safety designation by AHJ, SHARP Team. | Assigned to one asset (ie "ELITE" or system level asset) and covers the entire facility both Emergency and Exit Lights. Each Individual light has a maint code of PMHL for the Lights maintained as referenced in EEL docs. | N/A
Emer-Exit Lights Self Testing 2 | LV | ELV | ELV | Y | RTF | 0 |  | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Assigned to one asset (ie "ELITE" or system level asset) and covers the entire facility both Emergency and Exit Lights. Each Individual light has a maint code of RTF for the Lights maintained as referenced in EEL docs. | N/A
Engine-Fire | FIRE | FPS | PSY WWS FMT | Y | M1 | 0.08 | Check oil Check coolant Check batteries | Life Safety - NFPA 101 designation by Fire Systems SHARP Team. | Heavy Equipment personnel removed from weekly requirement | N/A
Engine-Fire | FIRE | FPS | PSY WWS FMT | Y | A1 | 1 |  | Life Safety NFPA 101 designation by Fire Systems SHARP Team SPCC Oil pan inspection |  | N/A
Engine-Trailer | CIVIL | HEQ | FMT | N | SA | 0.5 |  |  | Assets HE907848, HE907850, HE907854, HE907864. | N/A
ESS | FIRE | SEC | PSY | N | SA | 0.5 | Functional test Visual inspection | NFPA | Maintenance is equipment dependant. Security SHARP Team dissolved, Asset Category moved to this SHARP Team. | N/A
Excavator | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed | Manufacturer’s recommendation |  | N/A
Excavator-Gradall | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
Exit Lights | LV | ELV | ELV | Y | M1 | 0.08 | Functional test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Individual assets are indicated as PMHL. These are legacy fixtures. Not self-testing and therefore require to Monthly and Annual PM’s to insure the battery/lamps meet requirements. | N/A
Exit Lights | LV | ELV | ELV | Y | A1 | 1 | Functional test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Individual assets are indicated as PMHL. These are legacy fixtures. Not self-testing and therefore require to Monthly and Annual PM’s to insure the battery/lamps meet requirements. | N/A
Exit Lights-Self Testing | LV | ELV | ELV | Y | A1 | 1 | Self testing monthly requirement. Functional Annual test Visual inspection | NFPA-101 Life Safety designation by AHJ , SHARP Team. | Individual assets are indicated as PMHL. Monthly self-testing | N/A
Exit Lights-Self Testing 2 | LV | ELV | ELV | Y | RTF | 0 | Completely self-diagnostic | NFPA-101 Life Safety designation by AHJ , SHARP Team. | These fixtures perform both the Monthly and Annual tests automatically. Manual PMs not required. | N/A
FAA Obstruction Light | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Facility Lighting | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
FACP | FIRE | FPS | PSY | N | A1 | 1 | Visual inspection Component functional check | NFPA Includes components |  | N/A
Fall Prot | STRUCTURAL | STE | STR | N | A1 | 1 | Inspection of fall protection system Remove trolley and trolley stops and place in storage Install approved information tags on system Perform operational test | ANSI / OSHA |  | N/A
Fan Terminal Unit | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Fan-Exhaust-LT100HP | HVAC | HVC | HVC | N | RTF | 0 |  |  |  | N/A
Fan-Exhaust-LT100HP-Kitchen | HVAC | HVC | HVC | N | A1 | 1 | Clean blades Clean grease trap Visually check belts Lubricate Verify unit operational | Engineering analysis |  | N/A
Fan-Exhaust-LT100HP-LS | HVAC | HVC | HVC | N | M4 | 0.33 | Clean blades Clean grease trap Visually check belts Lubricate Verify unit operational | Engineering analysis | Hypergol / Fume Hood / Lab | N/A
Fan-Exhaust-MPPF Highbay | HVAC | HVC | HVC | N | SA | 0.5 | Clean blades Visually check belts Lubricate | Engineering analysis | No functional test to be performed during maintenance. | N/A
Fan-Exhaust-MPPF Highbay | HVAC | HVC | HVC | N | SA | 0.5 | Clean blades Visually check belts Lubricate | Engineering analysis | No functional test to be performed during maintenance. | N/A
Fan-Hood | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Fan-Pedestal | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Fan-Return | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Fan-Supply-LT100HP | HVAC | HVC | HVC | N | SA | 0.5 | Remove & replace filters. Drain condenser pan Condenser pan overflow switch operational Add anti-microbial tablets to condenser pan Verify no leaks Visually check belts and sheaves (replace/adjust). Verify unit operational. Clean coils and fan/blower Lubricate fan bearings (as required) Tighten fasteners (as required) | Engineering analysis |  | N/A
Fan-Supply-Smoke Control | FIRE | FPS | PSY | Y | A1 | 1 | End to end testing, to include operation of all equipment, measuring differential pressure across doorways, measuring force required to open doors with fans on. Fire alarm & HVAC crew effort | NFPA 92: Standard for Smoke Control Systems | NASA has not provided the test data from the final testing. BOSS OMD related to PM Job Plans will be on hold until it is obtained. OMD for assets and drawings can proceed. | N/A
FDC | FIRE | FPS | PSY WWS | N | SA | 0.5 |  |  | 9/9/14-Fire SHARP Team new Asset Category for Fire Departement Connections. | N/A
Fence | CIVIL | FEN | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Filters-Electronic | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Filters-HVC | HVAC | HVC | HVC | N | SA | 0.5 | Replace filters | Engineering analysis |  | N/A
Filters-HVC-CAIR-Local | HVAC | HVC | HVC | N | RTF | 0 |  |  |  | N/A
Filters-HVC-CAIR-Remote | HVAC | HVC | HVC | N | A1 | 1 | Replace filters | Engineering analysis |  | N/A
Filter-Sidestream | HVAC | HVC | HVC | N | RTF | 0 |  |  |  | N/A
Filters-Water | WATER | WTR | WWS | N | SA | 0.5 | Component replacement | Engineering analysis |  | N/A
Filters-Water-Humidifiers | WATER | WTR | WWS | N | RTF | 0 | N/A | Engineering analysis | Humidifier annual PM checks for scale buildup which would be an indicator that the filters need changed out. Very low water usage in the course of any year for these filters so PM is not required. | N/A
Fire-Deluge System | FIRE | FPS | PSY WWS | Y | A | 1 | Visual inspection Component functional check | NFPA Life Safety NFPA 101 designation by Fire Systems SHARP Team |  | N/A
Fire-Hose | FIRE | FPS | PSY WWS | N | A1 | 1 | Visual inspection Lubricate Component functional check |  |  | N/A
Fixed Spray | FIRE | FPS | PSY | Y | SA | 0.5 | Visual inspection Component functional check | NFPA Life Safety NFPA 101 designation by Fire Systems SHARP Team |  | N/A
Fixed Spray | FIRE | FPS | PSY | Y | A1 | 1 | Visual inspection Component functional check | NFPA Life Safety NFPA 101 designation by Fire Systems SHARP Team |  | N/A
Fixed Spray-1 | FIRE | FPS | PSY | Y | A1 | 1 | Visual inspection Component functional check | NFPA Life Safety NFPA 101 designation by Fire Systems SHARP Team | Assets in this category do not possess a flow switch, therefore the SA maintenance of the "Fixed Spray" category is not required. | N/A
Fixed Spray-2 | FIRE | FPS | PSY | Y | SA | 0.5 | Visual inspection Component functional check | NFPA Life Safety NFPA 101 designation by Fire Systems SHARP Team | Assets in this category are part of a simple system and do not require the code testing of the annual job plan used in the "Fixed Spray" category. | N/A
Floor | STRUCTURAL | STI | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Floor-Raised | STRUCTURAL | STI | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Flow Bench | HVAC | HVC | HVC | N | A1 | 1 | Replace Pre-filters. Inspect HEPA filters. Verify acceptable pressure drop and blower operation. | Engineering analysis |  | N/A
Foam | FIRE | FPS | PSY | N | W1 | 0.02 | System integrated test to a single asset number | NFPA | RLV only | N/A
Foam | FIRE | FPS | PSY | N | A1 | 1 | Visual inspection Component functional check | NFPA | RLV only | N/A
Fogger | CIVIL | HEQ | FMT | N | RTF | 0 | Run to failure/ equipment will be checked out when brought in for repair | Engineering analysis |  | N/A
Forklift-Diesel | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Forklift-Diesel | CIVIL | HEQ | FMT | N | A1 | 1 | Load Test | NASA 8719 9 | Load test not required on non-critical equipment. | N/A
Forklift-Electric | CIVIL | HEQ | FMT | N | M1 | 0.08 | Check condition of equipment, leaks, operation and safety Ensure battery is charged Check for damage to connectors, cables and cells Ensure cells and connections are clean Coat connectors with electrolyte grease Check specific gravity of each cell Check electrolyte level of cell, add distilled water as needed Verify holes in vent caps are clear Record hour meter reading | Manufacturer’s recommendation |  | N/A
Forklift-Electric | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Forklift-Electric | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | NASA 8719.9 | Load test not required on non-critical equipment. | N/A
Forklift-Gas | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Forklift-Gas | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Forklift-Gas | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | NASA 8719.9 | Load test not required on non-critical equipment. | N/A
Forklift-Jib Boom | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | NASA 8719. 9 | Load test not required on non-critical equipment. | N/A
Forklift-Lifting Fixture | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | NASA 8719.9 | Load test not required on non-critical equipment. | N/A
Forklift-Propane | CIVIL | HEQ | FMT | N | SA | 0.5 |  |  |  | N/A
Gas Piping | FIRE | FPS | PSY | N | TBD | TBD | TBD | TBD |  | N/A
Gates-Crash | CIVIL | FEN | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Gates-Motorized | CIVIL | FEN | STR | N | SA | 0.5 | Check electrical function | Engineering analysis |  | N/A
Gates-Motorized | CIVIL | FEN | STR | N | SA | 0.5 | Check mechanical function | Engineering analysis |  | N/A
Gearbox-Chiller | HVAC | HVC | HVC | N | SA | 0.5 | Oil Sampling | Manufacturer’s recommendation |  | N/A
Gearbox-HVAC | HVAC | HVC | HVC | N | SA | 0.5 | Oil Sampling | Manufacturer’s recommendation |  | N/A
Gearbox-HVAC | HVAC | HVC | HVC | N | Q1 | 0.25 | Vibration analysis data collection. | Manufacturer’s recommendation |  | N/A
Generator-Light Tower-Portable | LV | ELV | ELV | N | RTF | 0 | Ops check Check oil Check fuel General service | Engineering analysis | Service before Use - Service WON | N/A
Generator-Portable-Diesel | LV | ELV | ELV | N | RTF | 0 | Perform Visual inspection and load test prior to usage Check oil Check fuel General service | Engineering analysis | Service before Use - Service WON | N/A
Generator-Portable-Diesel-Program | LV | ELV | ELV | N | M1 | 0.083333 | Visual inspection | SPCC | Maintenance includes entire fuel system | N/A
Generator-Portable-Diesel-Program | LV | ELV | ELV | N | A1 | 1 | Extensive inspection | SPCC | Maintenance includes entire fuel system | N/A
Generator-Portable-Diesel-Program | LV | ELV | ELV | N | M1 | 0.083333 |  |  |  | N/A
Generator-Portable-Diesel-Program | LV | ELV | ELV | N | A1 | 1 |  |  |  | N/A
Generator-Portable-Diesel-SPCC | LV | ELV | ELV | N | M1 | 0.083333 | Visual inspection | SPCC | Maintenance includes entire fuel system | N/A
Generator-Portable-Diesel-SPCC | LV | ELV | ELV | N | A1 | 1 | Extensive inspection | SPCC | Maintenance includes entire fuel system | N/A
Generator-Portable-Gas | LV | ELV | ELV | N | RTF | 0 | Perform Visual inspection and repair as needed Check gas and oil | Engineering analysis | Corrective Maint only | N/A
Generator-Portable-Solar | LV | ELV | ELV | N | RTF | 0 | Perform Visual inspection and load test prior to usage | SHARP TEAM analysis |  | N/A
Generator-Stationary-Level 1 | MV | ELV | EHV | Y | W1 | 0.02 | Functional test Infrared scan Visual inspection Load test Clean/vacuum enclosure (interior & exterior). | NFPA 101 Life safety designation for Fire Systems SHARP Team |  | N/A
Generator-Stationary-Level 1 | MV | ELV | EHV | Y | M1 | 0.08 | Functional test Infrared scan Visual inspection Load test Clean/vacuum enclosure (interior & exterior). | NFPA 101 Life Safety - NFPA 101 designation by Fire Systems SHARP Team. | Monthly SPCC inspections are performed on many assets in this category. These are performed under PLTANKxxxM1 job plan. | N/A
Generator-Stationary-Level 1 | MV | ELV | EHV | Y | A1 | 1 | Functional test Infrared scan Visual inspection Load test Clean/vacuum enclosure (interior & exterior). | NFPA 101 Life Safety - NFPA 101 designation by Fire Systems SHARP Team. | Annual SPCC inspections are performed on many assets in this category. These are performed under PLTANKxxxA1 and PLPROCxxxA1 job plans. | N/A
Generator-Stationary-Level 2 | LV | ELV | ELV | N | M1 | 0.08 | Infrared scan | NFPA |  | N/A
Generator-Stationary-Level 2 | LV | ELV | ELV | N | A1 | 1 | Functional test Infrared scan Visual inspection Load test Clean/vacuum enclosure (interior & exterior). Oil Analysis | NFPA | On 500KW and larger a Insulation resistance test is performed. | N/A
Generator-Stationary-Level 2 | LV | ELV | ELV | N | A2 | 2 | Functional test Infrared scan Visual inspection Load test Clean/vacuum enclosure (interior & exterior). Oil Analysis | NFPA | On 500KW and larger a Insulation resistance test is performed. | PLGM09A2
Gradall | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Grader | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed Check and maintain fluid levels Inspect, clean and/or clear passageways, drains, vents, etc Inspect (visually or otherwise) to assess condition Perform lubrication activities Conduct an operational check Make adjustments as required Perform minor repair or initiate repair work order, as required Replace consumable parts or commodities (oil, filters, belts, etc) Collect and record asset data | Manufacturer’s recommendation |  | N/A
Grease Trap | WATER | WST | WWS | N | M1 | 0.08 | Inspect Pump out | Engineering analysis |  | N/A
Grounding | LV | ELV | ELV | N | A5 | 5 | Low Resistance Testing Visual inspection | NFPA-780, NASA STD-E-0012 | System level assets are maintained at a higher level (PMHL). | N/A
Grounding-Fence | LV | ELV | ELV | N | A5 | 5 | Low Resistance Testing Visual inspection | NFPA-780, NASA STD-E-0012 | System level assets are maintained at a higher level (PMHL). | N/A
Grounding-Floor | LV | ELV | ELV | N | SA | 0.5 | High Resistance Testing floor Visual inspection | NFPA-780, NASA STD-E-0012 | PHSF, MPPF, KDC | N/A
Grounding-Instr | LV | ELV | ELV | N | A5 | 5 | Low Resistance Testing Visual inspection | NFPA-780, NASA STD-E-0012 | System level assets are maintained at a higher level (PMHL). | N/A
Grounding-Ord | LV | ELV | ELV | N | A1 | 1 | Low Resistance Testing Visual inspection | NFPA-780, NASA STD-E-0012 | Ornance and hazardous commodity processing facilities | N/A
Grounding-Substation | LV | ELV | ELV | N | A1 | 1 | Low Resistance Testing Visual inspection | NFPA-780, NASA STD-E-0012 | Specific to C5 and Orsino | N/A
Gym Equipment | N/A | N/A | SPE | N | RTF | 0 |  | Engineering analysis | Located in the Astronaut quarters in M7-0355. | N/A
Halon | FIRE | FPS | PSY | N | SA | 0.5 | General Inspection |  |  | N/A
Handholes | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Heat Exchanger | HVAC | HVC | HVC | N | A1 | 1 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Engineering analysis |  | N/A
Heat Exchanger-Non-regulating | HVAC | HVC | HVC | N | RTF | 0 |  |  |  | N/A
Heat Recovery Unit | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Heat Recovery Wheel | HVAC | HVC | HVC | N | A1 | 1 | Remove & replace filters Verify unit operational Clean wheel Drain operational Condenser pan operational Verify no leaks Visually check belts (replace/adjust) Clean wheel Lubricate bearings Verify unit operational | Engineering analysis |  | N/A
Heat Recovery Wheel w/Filter | HVAC | HVC | HVC | N | A1 | 1 | Remove & replace filters Verify unit operational Clean wheel Drain operational Condenser pan operational Verify no leaks Visually check belts (replace/adjust) Clean wheel Lubricate bearings Verify unit operational | Engineering analysis |  | N/A
Heat Recovery Wheel w/Filter | HVAC | HVC | HVC | N | M2 | 0.16667 | Remove & Replace Filters. | Engineering analysis |  | N/A
Heater Blast Coil | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Heavy Equipment Misc | FIRE: CIVIL; FPS: HEQ; PSY: FMT; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Helipad | CIVIL |  | STR | N | A1 | 1 |  | Inspection |  | N/A
Hoist | EC&D | CRN | MEC | N | M1 | 0.08 | Inspection of chains, wire ropes, trolley, data tags and logbook Conduct electrical tests Perform operational test | ANSI / OSHA NASA 8519.9 | When used on a daily basis. Due to the variability in use and operating context some assets are maintained at different frequencies. | N/A
Hoist | EC&D | CRN | MEC | N | Q1 | 0.25 | Inspection of chains, wire ropes, trolley, data tags and logbook Conduct electrical tests Perform operational test | ANSI / OSHA NASA 8519.10 | When Standby or Idle | N/A
Hoist | EC&D | CRN | MEC | N | A1 | 1 | Same as Q Load Test (Remove) | ANSI / OSHA NASA 8519.9 | When Standby or Idle | N/A
Hook-Lifting | CIVIL | HEQ | FMT | N | A1 | 1 | Load Test | NASA 8719.9 |  | N/A
Hopper | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis | No Operating and FMC/PMC assets assigned at time of publication. | N/A
Hose-Washdown | Water | WST | WWS | N | RTF | 0 | N/A | Engineering evaluation |  | N/A
HTHW System | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Humidifier | HVAC | HVC | HVC | N | A1 | 1 | Clean reservoir Verify no leaks Verify operating nominally | Engineering analysis |  | N/A
HVAC EQP Room | HVAC | HVC | HVC | N | M1 | 0.08 |  | Operational Check |  | N/A
HVAC Misc | FIRE: HVAC; FPS: HVC; PSY: HVC; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Hydrant | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Component functional check | Engineering analysis |  | N/A
IEMS Location-Particle Counter | HVAC | HVC | HVC | N | PM | 1 | Remove device, install newly calibrated device, record asset # and calibration due date of replacement device | Engineering analysis | PM WONs will issue with due dates based on the Calibration Due Date of the installed transmitter asset. | N/A
IEMS Location-Temp-Humidity Trans. | HVAC | HVC | HVC | N | A1 | 1 | Remove device, install newly calibrated device, record asset # and calibration due date of replacement device | Engineering analysis | PM WONs will issue with due dates based on the Calibration Due Date of the installed transmitter asset. | N/A
Indicator-Digital | LV | ELV | ELV | N | A1 | 1 | CPMS Monitor Calibration |  |  | N/A
Instrumentation Xmitr | HVAC | HVC | HVC ELV/EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Inverter-LV | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | Solare inverters for solar farms | N/A
Inverter-LV GT 10KW | FIRE: LV; FPS: ELV; PSY: ELV
IPS | LV | ELV | ELV | Y | M1 | 0.08 | Functional test | SHARP Team analysis NFPA-101 | Instant Power System. | N/A
IPS | LV | ELV | ELV | Y | A1 | 1 | Same as M | SHARP Team analysis NFPA-101 | Instant Power System. | N/A
Isolation Disconnect Switch | MV | EHV | EHV | N | A2 | 2 | Infrared scan Resistance test Withstand test Visual Inspection Verify Grounding Clean insulators Lubricate moving current carrying parts Functional Test | NFPA 70B, NETA MTS and Engineering RCM analysis | All assets are located at Orsino (M6-0996) and at C5 (K6-1145) | PLDS014A2
Jet Starter | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis | No Operating and FMC/PMC assets assigned at time of publication. | N/A
Kitchen-Dishmachine | N/A | N/A | SPE | N | RTF | 0 |  | Engineering analysis | No industrial/commercial dishwashers are FMC. Current inventory of FMC assets are residential type and they have been changed to RTF. | N/A
Kitchen-Hood | STRUCTURAL | STI | SPE | N | W1 | 0.02 | Inspection of hood system Clean filters Lubricate Perform operational test | Engineering analysis | Lesser used assets (5) are performed W2 and M. | N/A
Kitchen-Misc Equipment | FIRE: N/A; FPS: N/A; PSY: SPE; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Kitchen-Oven | N/A | N/A | SPE | N | RTF | 0 |  |  | Remaining FMC assets no longer maintained by ISC | N/A
Kitchen-Range-Elect | N/A | N/A | SPE | N | RTF | 0 |  |  | Remaining FMC assets no longer maintained by ISC | N/A
Lab-Centrifuge | N/A | N/A | SPE | N | RTF | 0 |  | Engineering analysis | Most assets are at the OHF (M6-0495). | N/A
Ladder | CIVIL | HEQ | FMT | N | A1 | 1 | Load Test Inspection of various components | NFPA 1911 |  | N/A
Laminar Flow | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Lawn Sprinkler | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Leak Detector | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Lift | CIVIL | HEQ | FMT | N | A1 | 1 | Load Test | ANSI / OSHA |  | N/A
Lift | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed. Inspection Lubricate Adjust / replace various components Perform operational test | Manufacturer’s recommendation | Due to the variability in use and operating context some assets are maintained at different frequencies. Monthly (M1) required on assets that lift personnel. | N/A
Lift Station | WATER | WST | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Lift-Aerial | CIVIL | HEQ | FMT | N | M1 | 0.08 |  | Manufacturer’s recommendation |  | N/A
Lift-Aerial | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Inspection Lubricate Adjust / replace various components Perform operational test | Manufacturer’s recommendation | Due to the variability in use and operating context some assets are maintained at different frequencies. Monthly (M1) required on assets that lift personnel. SPCC inspections performed on 2 assets on a Q basis | N/A
Lift-Aerial | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | ANSI / OSHA |  | N/A
Lift-Aerial-Battery | CIVIL | HEQ | FMT | N | M1 | 0.08 | Operational test | Manufacturer’s recommendation |  | N/A
Lift-Aerial-Battery | CIVIL | HEQ | FMT | N | M1 | 0.08 | Battery test | Manufacturer’s recommendation |  | N/A
Lift-Aerial-Battery | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | ANSI / OSHA |  | N/A
Lift-Aerial-Battery | CIVIL | HEQ | FMT | N | A1 | 1 | Annual maintenance | Manufacturer’s recommendation |  | N/A
Lift-Aerial-Electric | CIVIL | HEQ | FMT | N | M1 | 0.08 | Operational test | Manufacturer’s recommendation |  | N/A
Lift-Aerial-Electric | CIVIL | HEQ | FMT | N | SA | 0.5 | Semi-annual maintenance | Manufacturer’s recommendation |  | N/A
Lift-Aerial-Electric | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | ANSI / OSHA |  | N/A
Lift-Boom | CIVIL | HEQ | FMT | N | M1 | 0.08 | Inspection | Engineering analysis |  | N/A
Lift-Boom | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Inspection Lubricate Adjust / replace various components Perform operational test | Manufacturer’s recommendation |  | N/A
Lift-Boom | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | ANSI / OSHA |  | N/A
Lift-Dock | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | N/A
Lift-Gate | CIVIL | HEQ | FMT | N | A1 | 1 | Load Test | ANSI / OSHA |  | N/A
Lifting Fixture | CIVIL | HEQ | FMT | N | A1 | 1 | Load test | ANSI / OSHA |  | N/A
Lift-Ladder | CIVIL | HEQ | FMT | N | A1 | 1 |  | Engineering analysis |  | N/A
Lift-Ladder | CIVIL | HEQ | FMT | N | A4 | 4 |  | Engineering analysis |  | N/A
Lift-Personnel | CIVIL | HEQ | FMT SPE | N | M1 | 0.08 | Load test Inspection Lubricate Adjust / replace various components Perform operational test | ANSI / OSHA | All lifts that lift people require a monthly. | N/A
Lift-Personnel | CIVIL | HEQ | FMT SPE | N | A1 | 1 | Load test Based on hours of operation to determine level of PM to be performed. Inspection Lubricate Adjust / replace various components Perform operational test | ANSI / OSHA | Quarterly maintenance no longer required per NASA STD 8719.9. Per conversation with NASA Lifting Standard 8719.9 Manager, Malcolm Glenn (KSC-SAG20), this level of maintenance is no longer required for these lift assets. Recommended level of maintenance is Annual PM and an Annual load test. | N/A
Lift-Platform | CIVIL | HEQ | FMT SPE | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed Inspect Lubricate Adjust various components Perform operational test | Manufacturer’s recommendation |  | N/A
Lift-Platform | CIVIL | HEQ | FMT SPE | N | A1 | 1 | Load test | ANSI / OSHA |  | N/A
Lift-Scissor | CIVIL | HEQ | FMT SPE | N | A1 | 1 | Load test | ANSI / OSHA | MAR S0346 - Recommended level of maintenance is Annual PM and an Annual load test. A limited number of assets have M battery testing. | N/A
Lift-Vehicle | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | N/A
Light Special | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | Targeted lighting systems Corrective Maintenance only | N/A
Lighting Contactor | LV | ELV | ELV | N | RTF | 0 | Repair or replace | Engineering analysis | Corrective maintenance WON | N/A
Lightning Prot | LV | ELV | ELV | N | A5 | 5 | Visual inspection Low resistance testing | NFPA 780, KSC-STD-012 | This is a higher level asset. System assets do not receive asset numbers. | N/A
Lightning Prot-ORD | LV | ELV | ELV | N | A1 | 1 | Visual inspection Low resistance testing | NFPA 780, KSC-STD-012 | Thisis a higher level asset. System assets do not receive asset numbers. Ornance and hazardous commodity processing facilities. | N/A
Lightning-Grounding | LV | ELV | ELV | N | A5 | 5 | Visual inspection Low resistance testing | NFPA 780, KSC-STD-012 | Thisis a higher level asset. System assets do not receive asset numbers. | N/A
Load Bank | LV | ELV | ELV | N | A1 | 1 | Functional test Infrared scan Visual inspection Clean /Vacuum enclosure (interior & exterior) | Engineering analysis |  | N/A
Load Break Switch | LV | ELV | ELV | N | SA | 0.5 | Infrared scan Visual inspection Check gas pressure | Engineering analysis |  | N/A
Load Tap Changer | LV | EHV | ELV | N | A2 | 2 |  |  |  | N/A
Load Tap Changer | LV | EHV | ELV | N | A4 | 4 |  |  |  | N/A
Loader | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Loader | CIVIL | HEQ | FMT | N | A1 | 1 | Same as A Inspect, clean and/or clear passageways, drains, vents, etc | Manufacturer’s recommendation |  | N/A
Loader-Skid Steer | CIVIL | HEQ | FMT | N | A1 | 1 |  | Manufacturer’s recommendation |  | N/A
LV Distribution | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | System level asset Maint code should be HO | N/A
Manholes | MV | EHV | EHV | N | A4 | 4 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Make adjustments as required. Collect and record asset data. Perform housekeeping activities. | Engineering analysis | Cable vaults are maintained on Q basis. | N/A
MCC | LV | ELV | ELV | N | A2 | 2 | Visual Inspection Clean Infra red Inspection Bus test Ops check breakers | Engineering analysis NFPA 70B | Added per SHARP direction 2016 | N/A
Meter-BTU | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis | Not PMed but read monthly. | N/A
Meter-IOPSS | WATER | WTR | WWS | N | A1 | 1 | R&T: Test batteries, Test UPS, Tighten all wire connections, check all for corrosion Verify: Signal strength, Sound Speed, SCNR | Mfg Recommended Maint. |  | N/A
Meter-Power | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | Not maintained but read monthly. | N/A
Meter-Water | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis | Not PMed but read monthly. | N/A
Missile Display | STRUCTURAL | STE | STR | N | A1 | 1 | Inspect to assess condition. Perform lubrication activities. Make adjustments as required. Perform housekeeping activities. | ANSI / OSHA |  | N/A
Mock-up | STRUCTURAL | STE | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Monitor-Oxygen | HVAC | HVC | HVC | N | SA | 0.5 | Review calibration report and verify calibration was completed successfully (passed). Attach a copy of the calibration report to this WON | Manufacturer’s Recommendation | Crew: ENGRHVAC | N/A
Monitor-Ozone | HVAC | HVC | HVC | N | A1 | 1 | Review calibration report and verify calibration was completed successfully (passed). Attach a copy of the calibration report to this WON | Manufacturer’s Recommendation | Crew: ENGRHVAC | N/A
Motor Circuit Protector | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Motor GE 150HP | LV | ELV | ELV | N | SA | 0.5 | Collect ferrographic data | Engineering analysis | All motors are located at UA or IACP. Assets at IACP are maintained at a higher level (PMHL). Due to the variability in configuration and operating context some assets are maintained at different frequencies. | N/A
Motor GE 150HP | LV | ELV | ELV | N | A3 | 3 | Functional test Infrared scan Visual inspection Insulation Resistance test Lubrication | Engineering analysis | All motors are located at UA or IACP. Assets at IACP are maintained at a higher level (PMHL). Due to the variability in configuration and operating context some assets are maintained at different frequencies. | N/A
Motor GE 75HP (U/A and IACP only) | LV | ELV | ELV | N | A1 | 1 | Functional test Infrared scan Visual inspection Insulation Resistance test Lubrication Vibration test | Engineering analysis | Primary Pumps at IACP | N/A
Motor LT 150HP | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Motor Starter | LV | ELV | ELV | N | RTF | 0 | Replace when defective | Engineering analysis | Corrective Maintenance WON | N/A
Mower-Attachment | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
MTS | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | Corrective Maintenance WON | N/A
Nets-Debris | STRUCTURAL | STI | STR | N | Q1 | 0.25 | Visual inspection Component functional check | Contractual requirement | Contract requirement. | N/A
Novec | FIRE | FPS | PSY | N | SA | 0.5 | Visual inspection Component functional check | NFPA |  | N/A
O2 Generator | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
ODMS | LV | ELV | ELV | Y | SA | 0.5 | Functional test Replace filter Visual inspection Clean /Vacuum enclosure (interior & exterior) Perform calibration (as required) | Life Safety designation by Fire Systems SHARP Team |  | PLUODMS PLU19456SA exceptions: R60xxxxxxQ - SSPF
ODMS-Test | LV | ELV | ELV | N | RTF | 0 | N/A |  | This Unit is only used for testing functionalities. It does not monitor any Oxygen deficient air. Not connected to the C3 Console or KCCS. This unit does not meet the requirements to be designated as life safety. | N/A
Oil Water Separator | HVAC | HVC | HVC | N | A1 | 1 | Remove/replace waste oil container. Sample. Replace filters. | Engineering analysis | The PMs for oil/water separator is worked at the same time as the accompanying air compressors therefore are PMHL. Assets are being maintained under the associated compressor PMs. The assets are parent-child and a note is is the RCM table. | CL806000A CP806001A Q9806001A
Ozone Generator | HVAC | HVC | HVC | N | A1 | 1 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. Perform housekeeping activities. | Engineering analysis | Five (5) ozone generators have M4 PMs. | HVCT001A HVCT139A HVAC92M4
Ozone Generator-BFF | HVAC | HVC | HVC | N | A1 | 1 |  | Manufacturer’s recommendation |  | HVACXXA
Ozone Generator-BFF | HVAC | HVC | HVC | N | M4 | 0.33 |  | Manufacturer’s recommendation |  | HVACXXM4
Pallet Jack - Maintained | CIVIL | HEQ | FMT | N | A | 1 | Load Test Battery check | KSC/NASA SAFETY | Assets interface with flight hardware | HEM003A HEM100A
Pallet Jack - Non Maintained | CIVIL | HEQ | FMT | N | RTF | 0 | N/A | None | Assets used to move pallets in logistics/warehouse | N/A
Panel-Compressor | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Panel-Control | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Panel-Flasher | LV | ELV | ELV | N | A1 | 1 | Functional test Infrared scan Visual inspection Clean /Vacuum enclosure (interior & exterior) | Engineering analysis Airport Lighting | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Panel-LV | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Parking Lots | CIVIL | PAV | RDG | N | A5 | 5 | Approximately 20% of the paved surfaces will be inspected per year | Engineering analysis | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
PDU | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Photocell | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Platform | CIVIL | HEQ | FMT | N | M1 | 0.08 | Battery test |  | Due to the variability in use and operating context some assets have additional maintenance. | N/A
Platform | CIVIL | HEQ | FMT | N | A1 | 1 | Load test |  | Due to the variability in use and operating context some assets have additional maintenance. | N/A
Platform-Helo | CIVIL | HEQ | FMT | N | SA | 0.5 | Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Manufacturer’s recommendation | Interchangeable with Lifts. | N/A
Platform-Wood | STRUCTURAL | STE | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Plumbing-General | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Poles - Concrete | STRUCTURAL | STR | RDG | N | A3 | 3 | Visual Inspection | PWS 3.15.1.4(3) |  | N/A
Poles - Fiberglass | STRUCTURAL | STR | RDG | N | A3 | 3 | Visual Inspection | PWS 3.15.1.4(3) |  | N/A
Poles - Metal-Exposed Anchor Bolts | STRUCTURAL | STR | RDG | N | A3 | 3 | Visual Inspection | PWS 3.15.1.4(3) |  | N/A
Poles - Metal-Metal Base | STRUCTURAL | STR | RDG | N | A3 | 3 | Visual Inspection | PWS 3.15.1.4(3) |  | N/A
Poles - Other | STRUCTURAL | STR | RDG | N | RTF | 0 |  |  |  | N/A
Poles-Wood | STRUCTURAL | STR | RDG | N | A3 | 3 | Visual Inspection | PWS 3.15.1.4(3) |  | N/A
Portable Light Bank | LV | ELV | ELV | N | RTF | 0 | Prior to use:Visual inspection, Functional Test | Engineering analysis |  | N/A
Port-o-lets | Water | WST | WWS | N | RTF | 0 | N/A | Engineering analysis |  | N/A
Power Supply-DC | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Power Unit-Hydraulic | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed Inspection Lubricate Adjust / replace various components Perform operational test | Manufacturer’s recommendation | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Pre-Action | FIRE | FPS | PSY | N | SA | 0.5 | Comply with Code requirements. Collect and record asset data. | NFPA |  | N/A
Pre-Action | FIRE | FPS | PSY | N | A1 | 1 | Comply with Code requirements. Collect and record asset data. | NFPA |  | N/A
Pre-Action | FIRE | FPS | PSY | N | A5 | 5 | Comply with Code requirements. Collect and record asset data. | NFPA |  | N/A
Pressure Control Valve | WATER | WTR | WWS | N | A1 | 1 |  |  |  | N/A
Pressure Control Valves | WATER | WTR | WWS | N | A1 | 1 | Check for proper operation | Engineering Analysis |  | N/A
Pressure Transducer | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Pressure Washer | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | N/A
Pressure Washer-Large | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
Pressure Washer-Small | CIVIL | HEQ | FMT | N | RTF | 0 |  | Manufacturer’s recommendation |  | N/A
Pressure-Relief | FIRE | FPS | PSY | N | A1 | 1 | Exercise and/or operate component(s) Inspect to assess condition | NFPA | VAB only. | N/A
Pump | WATER | WTR | FMT | N | RTF | 0 | Run to failure/ equipment will be checked out when brought in for repair | Engineering analysis |  | N/A
Pump | WATER | WTR | WWS | N | RTF | 0 | Run to failure/ equipment will be checked out when brought in for repair | Engineering analysis |  | N/A
Pump LT 10hp | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Pump-Chemical | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Pump-CHW-Portable | HVAC | HVC | HVC | N | PMHL | 0 | Verify unit is operating nominally Perform housekeeping | Engineering analysis | Verify proper operation of portable CHW pump as part of related Portable Chiller's PM prior to start of each hurricane season. | N/A
Pump-Dom | WATER | WTR | WWS | N | SA | 0.5 | Inspect, lubricate and clean rotating unit | Engineering analysis |  | N/A
Pump-Drain | WATER | WST | WWS | N | M1 | 0.08 | Visual inspection Component functional check Additive replacement | Engineering analysis |  | N/A
Pump-Fire | FIRE | FPS | PSY WWS | Y | M1 | 0.08 | Visual inspection Component functional check | NFPA Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Pump-Fire | FIRE | FPS | PSY WWS | Y | A1 | 1 | Flow rate validation Lubrication Exercise valves. | NFPA Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Pump-Fire-Diesel | FIRE | FPS | PSY WWS | Y | W1 | 0.02 | Visual inspection Component functional check Electrical check | NFPA 25, 8.2.2 Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Pump-Fire-Diesel | FIRE | FPS | PSY WWS | Y | A1 | 1 | Same as W. Flow rate validation | NFPA Life Safety - NFPA 101 designation by Fire Systems SHARP Team. |  | N/A
Pump-Fire-Jockey | FIRE | FPS | PSY WWS | N | RTF | 0 | Visual inspection Component functional check | NFPA | The annual for each of the sites that has a main fire pump and a jockey pump checks the pressure setting for the jockey pump but does no maintenance on the jockey pump. | N/A
Pump-Fire-Jockey/Freeze | FIRE | FPS | PSY WWS | N | W1 | 0.02 | Verify bearing oil level | Pumps maintain pressure at both Pads A and B and would supply freeze protection water | 100 gpm pumps are larger than most jockey pumps | N/A
Pump-Fire-Jockey/Freeze | FIRE | FPS | PSY WWS | N | A1 | 1 | Maintain the pumps annually | Pumps maintain pressure at both Pads A and B and would supply freeze protection water | 100 gpm pumps are larger than most jockey pumps | N/A
Pump-Fire-Jockey/Freeze | FIRE | FPS | PSY WWS | N | W1 | 0.02 | Verify bearing oil level | Pumps maintain pressure at both Pads A and B and would supply freeze protection water | 100 gpm pumps are larger than most jockey pumps | N/A
Pump-Fire-Jockey/Freeze | FIRE | FPS | PSY WWS | N | A1 | 1 | Maintain the pumps annually | Pumps maintain pressure at both Pads A and B and would supply freeze protection water | 100 gpm pumps are larger than most jockey pumps | N/A
Pump-Grove | CIVIL | HEQ | FMT | N | Q1 | 0.25 | Based on hours of operation to determine level of PM to be performed. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data | Manufacturer’s recommendation | Monthly and Annual SPCC inspections are performed on many assets in this category. These are performed under HETANKxxxxx job plan. | N/A
Pump-Grove-Auto | CIVIL | HEQ | FMT | N | W1 | 0.02 |  | Manufacturer’s recommendation |  | N/A
Pump-Grove-Auto | CIVIL | HEQ | FMT | N | Q1 | 0.25 |  | Manufacturer’s recommendation |  | N/A
Pump-Holding Tank | WATER | WTR | WWS | N | M1 | 0.08 | Exercise the pump monthly | Pump required to transfer water out of the holding tanks to the percolation areas | Tanks must have capacity to store IOP/SS launch and test flows | N/A
Pump-Holding Tank-Pad B | WATER | WTR | WWS | N | M1 | 0.08 | Exercise the pump monthly | Pump required to transfer water out of the holding tanks to the percolation areas | Tanks must have capacity to store IOP/SS launch and test flows | N/A
Pump-Holding Tank-Pad B | WATER | WTR | WWS | N | SA | 0.5 | Maintain the pumps semi-annually | Pump required to transfer water out of the holding tanks to the percolation areas | Tanks must have capacity to store IOP/SS launch and test flows | N/A
Pump-Pad Mount-(CHW/CW)-GT10HP | HVAC | HVC | HVC | N | SA | 0.5 | Inspect, lubricate and clean electric motor Verify operating properly | Engineering analysis | MAR S0219 removed A job plan HVBH11xxA 3/21/14 | N/A
Pump-Pad Mount-(CHW/CW)-Plant | HVAC | HVC | HVC | N | A1 | 1 |  | Engineering analysis |  | N/A
Pump-Pad Mount-(CHW/CW)-Plant | HVAC | HVC | HVC | N | SA | 0.5 |  | Engineering analysis |  | N/A
Pump-Pad Mount-(HTHW/HW)-GT10HP | HVAC | HVC | HVC | N | SA | 0.5 | Inspect, lubricate and clean electric motor Verify operating properly | Engineering analysis | MAR S0219 removed A job plan HVBH11xxA 3/21/14 | N/A
Pump-Pad Mount-(HTHW/HW)-Plant | HVAC | HVC | HVC | N | A1 | 1 |  | Engineering analysis |  | N/A
Pump-Pad Mount-(HTHW/HW)-Plant | HVAC | HVC | HVC | N | SA | 0.5 |  | Engineering analysis |  | N/A
Pump-Portable-SA | CIVIL | HEQ | FMT | N | SA | 0.5 | Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Pump-Primary Booster | WATER | WTR | WWS | N | M1 | 0.08 | Collect vibration data |  |  | N/A
Pump-Primary Booster | WATER | WTR | WWS | N | SA | 0.5 | Inspect, lubricate and clean rotating unit of pump | Engineering analysis |  | N/A
Pump-Recirc | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Pump-Secondary Booster | WATER | WTR | WWS | N | W1 | 0.02 | PERFORM WEEKLY RUNS, ALTERNATE PUMP IN OPERATION MONTHLY, PERFORM ANNUAL FLOW TESTING, CHECK OPERATION, CHECK FOR CORROSION, RUN EQUIPMENT, CHECK FOR COMPLIANCE WITH STANDARDS, ENTER ASSET CONDITION CODE | Engineering analysis |  | N/A
Pump-Secondary Booster | WATER | WTR | WWS | N | M1 | 0.08 | PERFORM WEEKLY RUNS, ALTERNATE PUMP IN OPERATION MONTHLY, PERFORM ANNUAL FLOW TESTING, CHECK OPERATION, CHECK FOR CORROSION, RUN EQUIPMENT, CHECK FOR COMPLIANCE WITH STANDARDS, ENTER ASSET CONDITION CODE | Engineering analysis |  | N/A
Pump-Secondary Booster | WATER | WTR | WWS | N | A1 | 1 | PERFORM WEEKLY RUNS, ALTERNATE PUMP IN OPERATION MONTHLY, PERFORM ANNUAL FLOW TESTING, CHECK OPERATION, CHECK FOR CORROSION, RUN EQUIPMENT, CHECK FOR COMPLIANCE WITH STANDARDS, ENTER ASSET CONDITION CODE | Engineering analysis |  | N/A
Pump-Sump | WATER | WST | HVC | N | RTF | 0 |  | Engineering analysis | The majority of sump pumps are small and require no maintenance to keep them operational | N/A
Pump-Surge Tank Sewage | WATER | WTR | WWS | N | SA | 0.5 |  |  |  | N/A
Pump-Vertical-(CHW/CW)-GT10HP | HVAC | HVC | HVC | N | SA | 0.5 | Functional test | Engineering analysis |  | N/A
Pump-Vertical-(CHW/CW)-Plant | HVAC | HVC | HVC | N | SA | 0.5 |  | Engineering analysis |  | N/A
Pump-Vertical-(CHW/CW)-Plant | HVAC | HVC | HVC | N | A1 | 1 |  | Engineering analysis |  | N/A
Pump-Waste Water | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
RCP | FIRE | FPS | PSY | N | SA | 0.5 | Semi-annual testing IAW NFPA 72/2001 | NFPA 72/2001
RCP | FIRE | FPS | PSY | N | A1 | 1 | Annual testing IAW NFPA 72/2001 | NFPA 72/2001
Reactor | HV | EHV | EHV | N | RTF | 0 |  |  |  | N/A
Receptacle | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Rectifier | LV | ELV | ELV | N | RTF | 0 |  |  |  | N/A
Reel-Service | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Reel-Washdown | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Refrigerant-Recovery System | HVAC | HVC | HVC | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
Refrigeration-Air Dryer | HVAC | HVC | HVC | N | A1 | 1 | Remove & replace filter media Verify delta temperatures (refrigerant charge) Perform housekeeping Verify unit operational | Engineering analysis | HVAC controls dryers are RTF | N/A
Refrigeration-Air Dryer-Controls | HVAC | HVC | HVC | N | RTF | 0 |  |  |  | N/A
Refrigeration-Freezer | HVAC | HVC | HVC | N | M4 | 0.33 | Verify delta temperatures (refrigerant charge) Clean coils Verify unit operational | Engineering analysis | CKARWRF002 are RTF. | N/A
Refrigeration-Ice Machine-Cube | HVAC | HVC | HVC | N | Q1 | 0.25 | Remove & replace filter Sanitize ice bin | Engineering analysis | Asset MYARWIM001 located KARS PARK excluded from Q1 requirement and changed to M4 to align with the MR HVC assets. Travel months to facility will be 4 months during the year. | N/A
Refrigeration-Ice Machine-Cube | HVAC | HVC | HVC | N | A1 | 1 | Same as Q Verify delta temperatures (refrigerant charge) Clean coils Verify unit operational | Engineering analysis |  | N/A
Refrigeration-Ice Machine-Flake | HVAC | HVC | HVC | N | Q1 | 0.25 | Remove & replace filter Sanitize ice bin | Engineering analysis | Maintenance depends on Asset location and usage. | N/A
Refrigeration-Ice Machine-Flake | HVAC | HVC | HVC | N | A1 | 1 | Same as Q Verify delta temperatures (refrigerant charge) Clean coils Verify unit operational | Engineering analysis | Maintenance depends on Asset location and usage. | N/A
Refrigeration-Refrigerator | HVAC | HVC | HVC | N | A1 | 1 | Verify delta temperatures (refrigerant charge) Clean coils Verify unit operational | Engineering analysis | Standard Refrigerators: OCARWRF001,OCARWRF002,OCARWRF005,OCARWRF006,OCARWRF007,OCARWRF008 at M7-0355, are RTF | N/A
Regulator-Constant Current | MV | EHV | EHV | N | A1 | 1 | Functional test Infrared scan Fluid analysis Visual inspection Operational check | Engineering analysis |  | N/A
Regulator-Constant Current | MV | EHV | EHV | N | A2 | 2 | Functional test Infrared scan Visual inspection Operational check | Engineering analysis |  | N/A
Reheat Coil | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Relays-LV | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | Sync Check relays | N/A
Relays-MV | LV | ELV | ELV | N | A2 | 2 | Functional test Infrared scan Visual inspection | Engineering analysis |  | N/A
Relays-Trip Units | LV | ELV | ELV | N | PMHL | 0 | Functional test Infrared scan Visual inspection Operational check | Engineering analysis | PMs for relay, bus and circuit breakers are now performed at the substation asset. Low Voltage Static Trip Units are considered part of the circuit breaker and will not stand alone. Static Trip Units will be tested / maintained during the Substation Secondary OC or other breaker test. After SHARP team review it was decided that there is no significant benefit to having separate assets for sub-components to the breakers. Trip units will be considered part of the breaker. | N/A
Resistor | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis | Per SHARP Team request PM added to asset MSE01NGR-1 only. (JP-PLH130A2 BIENNIAL) | N/A
Retrieval Device | CIVIL | N/A | SPE | N | RTF | 0 | Self Retracting Lifeline | Manufacturer's recommendation CAR 658 - 4/8/14 | No Operating and FMC/PMC assets assigned at time of publication. | N/A
Rigging | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | NASA 8719.9 ANSI / OSHA |  | N/A
Roof Ventilator | STRUCTURAL | ROF | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Roof Ventilator-Motor Op | STRUCTURAL | ROF | STR | N | RTF | 0 |  | Engineering analysis |  | N/A
Roof-BUR | STRUCTURAL | ROF | STR | N | A1 | 1 | Inspect integrity | Visual Inspection | Frequency is appropriate for a roof with high cost/benefit ratio. PM not required if roof is under 500 sf. | BSR009A
Roof-BUR-A2 | STRUCTURAL | ROF | STR | N | A2 | 2 | Inspect integrity | Visual Inspection | Frequency is appropriate for a roof with lower cost/benefit ratio. PM not required if roof is under 500 sf. | BSR009A2
Roof-Concrete | STRUCTURAL | ROF | STR | N | RTF | 0 |  | Engineering analysis | PM not required if roof is under 500 sf. | N/A
Roof-Fiberglass | STRUCTURAL | ROF | STR | N | RTF | 0 |  | Engineering analysis | PM not required if roof is under 500 sf. | N/A
Roof-LT 1000SF | STRUCTURAL | ROF | STR | N | RTF | 1 |  |  |  | N/A
Roof-Metal | STRUCTURAL | ROF | STR | N | A1 | 1 | Inspect integrity | Visual Inspection | Frequency is appropriate for a roof with high cost/benefit ratio. PM not required if roof is under 500 sf. | BSR004A
Roof-Metal-A2 | STRUCTURAL | ROF | STR | N | A2 | 2 | Maintenance and inspection ASTM’s roofing standards, inspections required to provide protection from external elements such as rain, sunlight, and heat | Visual Inspection | Frequency is appropriate for a roof with lower cost/benefit ratio. PM not required if roof is under 500 sf. | BSR004A2
Roof-PVC | STRUCTURAL | ROF | STR | N | A1 | 1 | Roof Inspection for PVC Roofing | Engineering analysis | Roof at M6-0570 | N/A
Roof-Shingle | STRUCTURAL | ROF | STR | N | A1 | 1 | Inspect integrity | Visual Inspection | Frequency is appropriate for a roof with high cost/benefit ratio. PM not required if roof is under 500 sf. | BSR003A
Roof-Shingle-A2 | STRUCTURAL | ROF | STR | N | A2 | 2 | Maintenance and inspection ASTM’s roofing standards, inspections required to provide protection from external elements such as rain, sunlight, and heat | Visual Inspection | Frequency is appropriate for a roof with lower cost/benefit ratio. PM not required if roof is under 500 sf. | BSR003A2
Roof-Single Ply | STRUCTURAL | ROF | STR | N | A1 | 1 | Inspect integrity | Visual Inspection | Frequency is appropriate for a roof with high cost/benefit ratio. PM not required if roof is under 500 sf. K8-1699 inspected SA | BSR0110A1
Roof-Single Ply-A2 | STRUCTURAL | ROF | STR | N | A2 | 2 | Maintenance and inspection ASTM’s roofing standards, inspections required to provide protection from external elements such as rain, sunlight, and heat | Visual Inspection | Frequency is appropriate for a roof with lower cost/benefit ratio. PM not required if roof is under 500 sf. | BSR011A2
Safety Signal Light | FIRE | SEC | ELV | N | RTF | 0 |  | Engineering analysis | Security SHARP Team dissolved, Asset Category moved to Fire SHARP Team. | N/A
Safety Stairs | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | NASA 8719.9 | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Sampler | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Saw | CIVIL | HEQ | FMT | N | RTF | 0 | Run to failure/ equipment will be checked out when brought in for repair | Engineering analysis |  | N/A
Saw-Large | CIVIL | HEQ | FMT | N | SA | 0.5 |  |  |  | N/A
Seal, Large Rubber | Water | WTR | WWS | N | SA | 0.5 | Inspect and grease | Engineering Analysis | Semi-annual check to verify operability | N/A
Sewage Treatment | WATER | WST | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Shackle Pin | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | NASA 8719.9 | 185 are maintained at a higher level (PMHL) | N/A
Shear | N/A | N/A | SPE | N | A1 | 1 | Inspect | Engineering analysis |  | N/A
Shoe Cleaner | N/A | N/A | SPE | N | RTF | 0 |  | Engineering analysis |  | N/A
Shwr-Eyewash | WATER | WTR | WWS | N | A1 | 1 | Operational Check | ANSI KNPR | Note: There is monthly operational checks performed by the Facility Manager. | N/A
Shwr-Eyewash-Portable-Gravity | WATER | WTR | WWS | N | RTF | 0 | N/A | Engineering analysis |  | N/A
Shwr-Eyewash-Portable-Pressurized | WATER | WTR | WWS | N | SA | 0.5 | Operational Check Fluid replacement | Engineering analysis | Two types of portable eyewash units: pressurized (Encon) and gravity feed (Fendalls) The pressurized units require change out of water every 180 days (semi-annual) The gravity feed (Ferndalls) units are RTF. No portable safety showers. | N/A
Sign | CIVIL | HEQ | FMT | N | RTF | 0 |  |  |  | N/A
Signs | CIVIL | STE | STR | N | TBD | TBD |  | Contractual requirement | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication.
Sling | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | NASA 8719.9 | 280 are maintained at a higher level (PMHL) | HEM106A HEM107A
Snatch Block | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | HEM107A
Solar PV system GT 5KW | FIRE: LV; FPS: ELV; PSY: ELV
Solar PV System LT 5KW | LV | ELV | ELV | N | PMHL | 0 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. Perform housekeeping activities. | Engineering analysis |  | PLPV001SA PLPV002SA
Sprayer | CIVIL | HEQ | FMT | N | RTF | 0 | Inspect (visually or otherwise) to assess condition. | Engineering analysis | Five assets are maintained on a SA frequency. | N/A
Spreader-Fert | CIVIL | HEQ | FMT | N | RTF | 0 | Conduct an operational check. | Engineering analysis |  | N/A
Stand | CIVIL | HEQ | FMT | N | A1 | 1 | Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Exercise and/or operate component(s). Inspect (visually or otherwise) to assess condition. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Standpipe | FIRE | FPS | PSY WWS | N | A1 | 1 | Visual inspection Valve functional check | NFPA |  | N/A
Standpipe | FIRE | FPS | PSY WWS | N | A5 | 5 | Visual inspection Valve functional check | NFPA |  | N/A
Storm Water Ponds | CIVIL | STM | RDG | N | RTF | 0 | Inspections Performed as Per Regulatory Requirements. Inspection Performed by ISC Environmental | Engineering analysis | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Structure | STRUCTURAL | STE | STR | N | RTF | 0 |  | Paint Plan Corrosion Control Plan Maintenance Strategy is plan driven, based upon contractual requirements and inspections. |  | N/A
Substation Secondary | LV | ELV | ELV | N | A4 | 4 |  |  |  | N/A
Substation-LV-Draw Out | LV | ELV | ELV | N | A2 | 2 | Operationally test breakers Test trip units Manual and auto tests of switchgear and breakers Remote test of breakers and monitoring PLC/Trip unit Battery replacement | NFPA 70B, NETA MTS Engineering analysis | Operational Check | N/A
Substation-LV-Draw Out | LV | ELV | ELV | N | A4 | 4 | Perform insulation test on substation and breakers Operationally test Breakers Clean & lubricate substation cubicles & breakers. | NFPA 70B, NETA MTS Engineering analysis | Substation PM | N/A
Substation-LV-Hybrid | LV | ELV | ELV | N | A2 | 2 | Operationally test breakers Test trip units Manual and auto tests of switchgear and breakers Remote test of breakers and monitoring PLC/Trip unit Battery replacement | NFPA 70B, NETA MTS Engineering analysis | Operational Check | N/A
Substation-LV-Hybrid | LV | ELV | ELV | N | A4 | 4 | Perform insulation test on substation and breakers Operationally test Breakers Clean & lubricate substation cubicles & breakers. | NFPA 70B, NETA MTS Engineering analysis | Substation PM | N/A
Substation-LV-Molded Case | LV | ELV | ELV | N | A4 | 4 | Perform insulation test on substation Operationally test Breakers Clean substation enclosure | NFPA 70B, NETA MTS Engineering analysis | Substation PM | N/A
Sweeper | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Engineering analysis | Floor sweeper | N/A
Sweeper-SLF | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Sweeper-SLF | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed. Same as SA Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc) | Manufacturer’s recommendation |  | N/A
Switchboard | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Switchgear | MV | EHV | EHV | N | A2 | 2 | Functional test Infrared scan Visual inspection Clean/vacuum enclosure (interior & exterior) | Engineering analysis |  | N/A
Switch-Primary | MV | EHV | EHV | N | A4 | 4 | Functional test Infrared scan Visual inspection Clean & vacuum inside and outside the enclosure. | Engineering analysis |  | N/A
Switchyard | MV | EHV | EHV | N | Q1 | 0.25 | Functional test Infrared scan Visual inspection Clean/vacuum enclosure (interior & exterior) | Engineering analysis |  | N/A
System | VARIOUS | VAR | VAR | N | HO | 0 |  |  | Placeholder assets used for hierarchy purposes only. | N/A
Tanks-Demin H2O | WATER | WTR | WWS HVC | N | RTF | 0 |  | Engineering analysis | Labs call shop and put in requiest when they believe tanks need to be cleaned. No specific interval for cleaning. Strictly based on analysis of water in tank. | N/A
Tanks-Domestic Hot H2O | WATER | WTR | WWS HVC | N | RTF | 0 | N/A | Engineering analysis |  | N/A
Tanks-Elev | WATER | WTR | WWS | N | A5 | 5 | Create statement of work, obtain certified contractor to inspect the IOP/SS elevated water tank, structure and riser | BOSS requirement to have inspected every 5 years |  | N/A
Tanks-Expansion-CW | HVAC | HVC | HVC | N | A1 | 1 | Verify tank is not completely filled Drain the tank to an acceptable level, as required Verify unit operational | Engineering analysis |  | N/A
Tanks-Expansion-HW | HVAC | HVC | HVC | N | A1 | 1 | Verify tank is not completely filled Drain the tank to an acceptable level, as required Verify unit operational | Engineering analysis |  | N/A
Tanks-Fire | FIRE | FPS | PSY WWS | N | Q1 | 0.25 | Inspect support structure, catwalks and ladders, expansion joints, and surrounding area | NFPA 25, 9.2 | Annual expansion joints inspection is included | N/A
Tanks-Fire | FIRE | FPS | PSY WWS | N | SA | 0.5 | Same as Q Test Alarm Levels | NFPA 25, 9.2 NFPA 25, 9.3.5 |  | N/A
Tanks-Fire | FIRE | FPS | PSY WWS | N | A5 | 5 | Same as SA Visual inspection of interior | NFPA 25, 9.2 NFPA 25, 9.3.5 NFPA 25, 9.2.6.1.2 |  | N/A
Tanks-Fire Suppression | WATER | WTR | WWS HVC | N | Q1 | 0.25 | Operational check and Inspection | NFPA |  | N/A
Tanks-Fire Suppression | WATER | WTR | WWS HVC | N | SA | 0.5 | Operational check and Inspection | NFPA |  | N/A
Tanks-Fire-Surge | FIRE | FPS | PSY WWS | N | SA | 0.5 | Visual inspection | NFPA |  | N/A
Tanks-Fire-Surge | FIRE | FPS | PSY WWS | N | A1 | 1 | Visual inspection | NFPA | Hydro-Pneumatic Tanks | N/A
Tanks-Fuel | ENV | ENV | ELV/EHV FMT STR | N | M1 | 0.08 | Visual inspection | SPCC | Maintenance for PL and HVC includes entire fuel system | N/A
Tanks-Fuel | ENV | ENV | ELV/EHV FMT STR | N | A1 | 1 | Extensive inspection | SPCC | Maintenance for PL and HVC includes entire fuel system | N/A
Tanks-Fuel | ENV | ENV | ELV/EHV FMT STR | N | A1 | 1 | Extensive inspection | REGISTERED | Maintenance for PL and HVC includes entire fuel system. The registered tanks with an interstitial valve (or monitoring device) do NOT require annual inspection. The Release Detection device shall be tested annually to ensure proper operation for tanks using the Krueger At-A Glance leak gauge. | N/A
Tanks-Fuel-Mobile | ENV | ENV | ELV/EHV FMT STR | N | M1 | 0.08 | Inspection | SPCC |  | N/A
Tanks-Fuel-Mobile | ENV | ENV | ELV/EHV FMT STR | N | A1 | 1 | Inspection | SPCC |  | N/A
Tanks-H2O | WATER | WTR | WWS HVC | N | A1 | 1 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Engineering analysis | WWS: Tanks must be cleaned annually to maintain water quality required by customer. | N/A
Tanks-H2O-Pad B | WATER | WTR | WWS HVC | N | A1 | 1 | Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Engineering analysis | WWS: Tanks must be cleaned annually to maintain water quality required by customer. | N/A
Tanks-H2O-Pad B | WATER | WTR | WWS HVC | N | A5 | 5 |  | FDEP Requirement |  | N/A
Tanks-H2O-W-5 Pump Station | WATER | WTR | WWS HVC | N | A5 | 5 | Operational Check and Inspection | FDEP Requirement |  | N/A
Tanks-IWW | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis | Waste water retention. | N/A
Tanks-Make Up Water | HVAC | HVC | HVC WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Tanks-O2 | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Tanks-Septic | WATER | WST | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Tanks-TBD | FIRE: N/A; FPS: N/A; PSY: WWS; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
TAWS | FIRE | SEC | PSY | N | A1 | 1 | Inspect (visually or otherwise) to assess condition. Conduct an operational check. | NFPA | Tornado Area Warning System | N/A
Terminal Boxes | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Test Equipment | LV | ELV | ELV | N | RTF | 0 |  | Engineering analysis |  | N/A
Test Weight | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | NASA 8719.9 | MAR S0489 add new Test Weight asset category per CAR 664. Test Weight assets to be PMHL. A PM parent TWP001 representing a 10% random sampling of the test weight population. | N/A
TIDS | FIRE | SEC | PSY | N | RTF | 0 |  | Engineering analysis | Tactical Intrusion Detection Device | N/A
Tool-Office | FIRE: N/A; FPS: N/A; PSY: SPE; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Tools-Shop | FIRE: N/A; FPS: N/A; PSY: SPE; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Tow Bar | CIVIL | HEQ | FMT | N | SA | 0.5 | Check and maintain fluid levels. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Make adjustments as required. Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Tower | STRUCTURAL | STE | STR | N | A3 | 3 | Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Engineering analysis | Theis asset category has assets that are mechanical in nature and not a structural tower. | N/A
Toxic-HVC | HVAC | ENV | HVC | Y | A1 | 1 | Annual testing of HVAC shutdowns by/with fire alarm | KSC – BOSS contract & local customer requirement | Integrated with fire alarm. Separate system designation in OMEU intentionally | HVACBAS01A
Track Hoe | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Tracked vehicle Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Tractor | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Traffic | FIRE | SEC | PSY | N | A1 | 1 | Visual inspection Component functional check | MUTC | Security SHARP Team dissolved, Asset Category moved to Fire SHARP Team. | N/A
Trailer | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data | Manufacturer’s recommendation | Due to the variability in types of Trailer, their use and operating context some assets have additional maintenance. | N/A
Trailer-Boat | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
Trailer-Cable Reel | CIVIL | HEQ | FMT | N | SA | 0.5 | Maintenance | Manufacturer’s recommendation |  | N/A
Trailer-Cable Reel | CIVIL | HEQ | FMT | N | A1 | 1 | Maintenance | Manufacturer’s recommendation |  | N/A
Trailer-Cargo | CIVIL | HEQ | FMT | N | A1 | 1 |  | Manufacturer’s recommendation |  | N/A
Trailer-Cargo | CIVIL | HEQ | FMT | N | M1 | 0.08 |  |  | Regulatory Inspection | N/A
Trailer-Dust Collector | CIVIL | HEQ | FMT | N | Q | 0.25 | Maintenance, manufactures recommendation | Manufacturer’s recommendation |  | N/A
Trailer-Fuel Tank | CIVIL | HEQ | FMT | N | A1 | 1 |  | Manufacturer’s recommendation |  | N/A
Trailer-Fuel Tank | CIVIL | HEQ | FMT | N | M1 | 0.08 |  |  | Regulatory Inspection | N/A
Trailer-Special Use | CIVIL | HEQ | FMT | N | RTF | 0 |  |  |  | N/A
Transformers-Dry-Instrument | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Transformers-Dry-LV | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Transformers-Dry-MV | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Transformers-Instrument | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Transformers-Oil-MV | MV | EHV | EHV | N | A2 | 2 | Infrared scan Visual inspection Power Factor Test Hipot test DGA Analysis | Engineering analysis |  | N/A
Transformers-Oil-Pole | MV | EHV | EHV | N | RTF | 0 |  | Engineering analysis |  | N/A
Transformers-Oil-Power-C5/Orsino | MV | EHV | EHV | N | Q1 | 0.25 | Infrared scan | Engineering analysis |  | N/A
Transformers-Oil-Power-C5/Orsino | MV | EHV | EHV | N | A1 | 1 | Same as Q Oil Test | Engineering analysis |  | N/A
Transformers-Oil-Power-C5/Orsino | MV | EHV | EHV | N | A2 | 2 | Same as A Visual inspection Power Factor Test Hipot test DGA Analysis | Engineering analysis |  | N/A
Translucent Panels | STRUCTURAL | STE | STR | N | RTF | 0 |  | Engineering analysis | All panels are in the VAB (K6-0848) and the assets represent the interior and exterior. | N/A
Transmitter-Pressure | LV | ELV | ELV | N | PMHL | 0 |  |  |  | PLGM0010A1
Transmitter-Pressure | LV | ELV | ELV | N | PMHL | 0 |  |  |  | PLGM0010A1
Transmitter-Temperature | LV | ELV | ELV | N | PMHL | 0 |  |  |  | PLGM0010A1
Transmitter-Temperature | LV | ELV | ELV | N | PMHL | 0 |  |  |  | PLGM0010A1
Transmitter-Temp-Humidity | HVAC | HVC | HVC | N | PMHL | 0 | Remove device, install newly calibrated device, record asset # and calibration due date of replacement device | Engineering analysis | Transmitter asset will be maintained under a PM WON issued against the Location asset where the transmitter is in operation. | HVCAL001A1
Truck Restraint | CIVIL | HEQ | FMT | N | RTF | 0 |  | Engineering analysis |  | N/A
Truck-Bridge | CIVIL | HEQ | FMT | N | A1 | 1 |  | Engineering analysis |  | N/A
Truck-Bridge | CIVIL | HEQ | FMT | N | Q1 | 0.25 |  | Manufacturer’s recommendation | Load Test | N/A
Truck-Bridge | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Engineering analysis |  | N/A
Truck-Bridge | CIVIL | HEQ | FMT | N | M1 | 0.08 |  | Engineering analysis |  | N/A
Truck-Bucket | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Inspect (visually or otherwise) to assess condition. Check and maintain fluid levels. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Truck-Bucket | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | ANSI / OSHA |  | N/A
Truck-Fire | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. Perform housekeeping activities. | Manufacturer’s recommendation |  | N/A
Truck-Fire | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed | Manufacturer’s recommendation |  | N/A
Truck-Fire | CIVIL | HEQ | FMT | N | A2 | 2 | Based on hours of operation to determine level of PM to be performed | Manufacturer’s recommendation |  | N/A
Truck-Fire-ARFF | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. Perform housekeeping activities. | Manufacturer’s recommendation |  | N/A
Truck-Fuel | CIVIL | HEQ | FMT | N | A1 | 1 |  | Manufacturer’s recommendation | Regulatory Inspection | N/A
Truck-Fuel | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Truck-General | CIVIL | HEQ | FMT | N | SA | 0.5 |  | Manufacturer’s recommendation |  | N/A
Truck-Hi-Ranger | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Truck-Hi-Ranger | CIVIL | HEQ | FMT | N | A1 | 1 | Load test Inspection | ANSI / OSHA |  | N/A
Truck-Ladder Platform | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. Perform housekeeping activities. | Manufacturer’s recommendation |  | N/A
Truck-MRAP | CIVIL | HEQ | FMT | N | A | 1 | Based on hours of operation to determine level of PM to be performed. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Collect and record asset data. | Manufacturer’s recommendation | NASA requested frequency to be changed from SA to A. (MAR FPX0333) | N/A
Truck-Rescue | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Exercise and/or operate component(s). Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Truck-Rescue | CIVIL | HEQ | FMT | N | A1 | 1 | Based on hours of operation to determine level of PM to be performed Same as SA | Manufacturer’s recommendation |  | N/A
Truck-SWAT | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Truck-TBD | FIRE: CIVIL; FPS: HEQ; PSY: FMT; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Tug | CIVIL | HEQ | FMT | N | SA | 0.5 | Based on hours of operation to determine level of PM to be performed. Check and maintain fluid levels. Inspect, clean and/or clear passageways, drains, vents, etc. Inspect (visually or otherwise) to assess condition. Perform lubrication activities. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Replace consumable parts or commodities (oil, filters, belts, etc). Collect and record asset data. | Manufacturer’s recommendation |  | N/A
Tug-Electric | CIVIL | HEQ | FMT | N | M1 | 0.08 |  | Manufacturer’s recommendation |  | N/A
Tug-Electric | CIVIL | HEQ | FMT | N | Q1 | 0.25 |  | Manufacturer’s recommendation |  | N/A
Tunnel | STRUCTURAL | STE | STR | N | A2 | 2 | Visually Inspect Tunnel, provide any adverse findings in writing | N/A | NASA requested via SHARP team | N/A
Turnstile | SECURITY | SEC | PSY | N | SA | 0.5 | Inspection, Cleaning, Operational Check | Engineering analysis |  | N/A
UPS-Life Safety | LV | ELV | ELV | Y | SA | 0.5 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis | The lights associated with this asset are tested M and A per NFPA. | N/A
UPS-Life Safety | LV | ELV | ELV | N | A1 | 1 |  | IEEE NETA MTS Engineering Analysis | The lights associated with this asset are tested M and A per NFPA. | N/A
UPS-Self Contained | LV | ELV | ELV | N | SA | 0.5 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis |  | N/A
UPS-Self Contained | LV | ELV | ELV | N | A1 | 1 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis |  | N/A
UPS-Self Contained Small | LV | ELV | ELV | N | SA | 0.5 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis |  | N/A
UPS-Self Contained Small | LV | ELV | ELV | N | A2 | 2 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis |  | N/A
UPS-With External Battery | LV | ELV | ELV | N | SA | 0.5 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis |  | N/A
UPS-With External Battery | LV | ELV | ELV | N | A1 | 1 | Functional test Visual inspection Clean/vacuum enclosure (interior & exterior) Replace filters Load test batteries | IEEE NETA MTS Engineering Analysis |  | N/A
Vacuum Circuit Recloser | MV | EHV | EHV | N | A1 | 1 |  | Category was returned upon request of SHARP Team. |  | N/A
Vacuum Contactor 5KV | MV | EHV | EHV | N | A4 | 4 |  |  | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Vacuum Fault Interrupter | MV | EHV | EHV | N | SA | 0.5 | Infrared scan | Engineering analysis |  | N/A
Vacuum Fault Recloser | MV | EHV | ELEC | N | A2 | 2 |  | Engineering Analysis | 2 Assets VFR-100 & VFR-797 per SE | N/A
Vacuum Producer | HVAC | HVC | HVC | N | SA | 0.5 | Check belts Empty debris Perform housekeeping Verify unit operational | Engineering analysis |  | N/A
Vacuum Producer-High Use | HVAC | HVC | HVC | N | SA | 0.5 | Check belts Empty debris Perform housekeeping Verify unit operational | Engineering analysis |  | N/A
Vacuum Producer-High Use | HVAC | HVC | HVC | N | M | 0.08 | Empty debris Verify unit operational | Engineering analysis |  | N/A
Vacuum Pump | HVAC | HVC | HVC | N | A1 | 1 | Change oil | Engineering analysis |  | N/A
Valve-Isolation | Water | WST | WWS | N | PMHL | 0 | N/A | Engineering evaluation |  | N/A
Valves-Check | Water | WST | WWS | N | PMHL | 0 | N/A | Engineering evaluation |  | N/A
Valves-Control | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Valves-Fire | FIRE | FPS | PSY | N | A1 | 1 | Visual inspection Component functional check | Engineering analysis | Some assets in this category are maintained at a higher level (PMHL) | N/A
Valves-Fire Hose | FIRE | FPS | PSY | N | A1 | 1 | Visual inspection Component functional check | NFPA | 9/9/14-Per Fire SHARP Team Q PMs are no longer required. | N/A
Valves-Fire Hose | FIRE | FPS | PSY | N | A5 | 5 | Visual inspection Component functional check | NFPA | 9/9/14-Per Fire SHARP Team Q PMs are no longer required. | N/A
Valves-Fire Supply | FIRE | FPS | PSY WWS | N | A1 | 1 | Visual inspection Component functional check | NFPA |  | N/A
Valves-Float | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Component functional check | NFPA 25, 9.5 | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication. | N/A
Valves-Gate | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Component functional check | Engineering analysis |  | N/A
Valves-Knife | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Component functional check | Engineering analysis |  | N/A
Valves-PIV | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Component functional check | Engineering analysis |  | N/A
Valves-PRV | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Component functional check | Engineering analysis | Not required on 2” or smaller unless it feeds a Safety shower or eyewash | N/A
Valves-PRV-2" or smaller | WATER | WTR | WWS | N | RTF | 0 | N/A | Engineering analysis | PM Not required on 2” or smaller unless it feeds a Safety shower or eyewash | N/A
Valves-Sound Suppression | FIRE | IOP | WWS | N | A1 | 1 | Visual inspection Clean Lubricate | Engineering analysis | All assets are located at Pad B. | N/A
Valves-Sound Suppression | FIRE | IOP | WWS | N | A2 | 2 | Same as A. Exercise | Engineering analysis | All assets are located at Pad B. | N/A
Valves-Sound Suppression | FIRE | IOP | WWS | N | SA | 0.5 | Inspect, Lube and operational check | Engineering Analysis | Annual check to verify operability | N/A
Valves-TBD | FIRE: WATER; FPS: WTR; PSY: WWS; N: N | Place holder for unique assets with no commonality or insufficient data to assign to an asset category No recommended maintenance strategy is applied | N/A
Valves-Washdown | Water | WTR | WWS | N | A1 | 1 | Inspect (visually or otherwise) to assess condition. Conduct an operational check. Make adjustments as required. Perform minor repair or initiate repair work order, as required. Collect and record asset data. | Engineering analysis | Annual check to verify operability | N/A
VAV Box | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Vehicle-Utility | CIVIL | HEQ | FMT | N | SA | 0.5 |  |  |  | N/A
Vehicle-Utility-Gator | CIVIL | HEQ | FMT | N | RTF | 0 |  |  |  | N/A
VFD | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Washer-Dryer | N/A | N/A | SPE | N | RTF | 0 |  | Engineering analysis |  | N/A
Waste Treatment | WATER | WST | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Water Detectors | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Water Dist System | WATER | WTR | WWS | N | A2 | 2 | Visual inspection Component functional check | Engineering analysis |  | N/A
Water Fountain | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Water Heater | WATER | WTR | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Water Interface | WATER | WTR | WWS | N | A1 | 1 | Visual inspection Clean Lubricate | Engineering analysis | MLP Interfaces | N/A
Water Softener | WATER | WTR | WWS | N | M1 | 0.08 | Visual inspection Component functional check | Engineering analysis |  | N/A
Water Softener-A/C | HVAC | HVC | HVC | N | RTF | 0 |  | Engineering analysis |  | N/A
Water Treatment | WATER | WST | WWS | N | RTF | 0 |  | Engineering analysis |  | N/A
Water Treatment-DI | WATER | WTR | WWS | N | TBD | TBD |  |  |  | TBD
Weather Arm | FIRE: STRUCTURAL; FPS: STE; PSY: STR; N: N | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication.
Weather Equipment | FIRE: LV; FPS: ELV; PSY: ELV
Welder | CIVIL | HEQ | SPE | N | Q1 | 0.25 | Inspect (visually or otherwise) to assess condition. Perform maintenance per manufacturer’s recommendation. Conduct an operational check. Collect and record asset data. Perform housekeeping activities. | Engineering analysis |  | BSM039Q
Wet Chem | FIRE | FPS | PSY | N | SA | 0.5 | Comply with Code requirements Collect and record asset data | NFPA | Delaware North systems have a W2 frequency assigned. | PSWC01xxSA PSWC05xxSA PSWC06xxSA PSWC11xxSA
Wet Chem | FIRE | FPS | PSY | N | A1 | 1 | Comply with Code requirements Collect and record asset data | NFPA |  | PSWC01xxxA PSWC05xxxA PSWC06xxxA
Wet Pipe | FIRE | FPS | PSY | N | A1 | 1 | Comply with Code requirements Collect and record asset data | NFPA |  | PSSP001xxA PSSP004xxA PSSP007xxA PSSPC01xxA
Wireless Lockset | FIRE | FPS | PSY | N | A1 | 1 |  |  |  | PSTC20000A
Wireless System | FIRE | FPS | PSY | N | TBD | TBD | TBD | TBD
Wireless System | FIRE | SEC | PSY | N | A1 | 1 |  |  |  | PSWSINXXXA
WWS-Misc | FIRE: WATER; FPS: WTR; PSY: WWS; N: N | No CLIN customer, Operating and FMC/PMC assets assigned at time of publication.

## Legend
Maintenance Plan Appendix A Formatting
Column Name | Column Definition
Asset Category | A grouping of common or like assets which serve as the basis for the implementing the maintenance standard. An Asset Category may appear multiple times to show more than one frequency or different types of maintenance.
SHARP Team | This is the SHARP team that has primary responsibility for the Asset Category, Assets assigned and overall maintenance. Individual assets retain their assignments to the responsible SE. Refer to SHARP Team Systems Breakdown, ENG-REF-0026.
The SHARP Teams are currently defined as:
· CIVIL - Civil and Heavy Equipment
· EC&D - Elevators, Cranes and Doors
· FIRE - Fire Safety, Fire Suppression, Deluge, Protective Systems
· HVAC - Heating, Ventilation, and Air Conditioning, and Compressed Air
· LV - Low Voltage
· MV - Medium/High Voltage
· STRUCTURAL - Facilities, Buildings, Bridges
· WATER - Water, Plumbing, and Waste Water
· N/A - No applicable SHARP Team assignment
LRP System | The Long Range Planning (LRP) system that the Asset Category is aligned with for Annual Work Plan and Local Authority funding purposes.
· ABS - Asbestos Abatement
· AIR - Compressed Air
· BRG - Bridges
· CCS - Corrosion Control Systems
· CPS - Cathodic Protection Systems
· CRN - Cranes
· CTL - Controls
· DEM - Demolition
· DOR - Doors
· EHV - Electrical-High Voltage
· ELE - Elevators
· ELV - Electrical-Low Voltage
· ENR - Energy
· ENV - Environmental
· FEN - Fencing
· FPS - Fire Protection Systems
· FUL - Fuels
· GND - Grounds, Landscaping
· HEQ - Heavy Equipment
· HVC - Heating, Ventilation and Air Conditioning, and Compressed Air
· IOP - Sound Supression
· N/A - Not Applicable
· PAE - Paint-Exterior
· PAI - Paint-Interior
· PAV - Pavements
· ROF - Roofing
· SEC - Security Systems
· STE - Structural Exterior
· STI - Structural Interior
· STM - Storm Water
· STR - Structural
· TWR - Towers
· WST - Wastewater Treatment
· WTR - Water Distribution
Maximo System | A legacy contract system classifier for the asset which is also the top level of a failure hierarchy. Two or more entries in this column indicate the Asset Category is shared by multiple systems.
· EHV - High Voltage
· ELV - Low Voltage
· FMT - Fleet Management Systems
· HVC - Heating, Ventilation and Air Conditioning, and Compressed Air
· MEC - Mechanical
· PSY - Protective Systems
· RDG - Roads and Grounds
· SPE - Special Equipment
· STR - Structural
· WWS - Water and Waste Systems
Life Safety | A “Y” indicates the Asset Category and Assets assigned are Life Safety in accordance with NFPA 101 as determined by the Fire Systems SHARP Team.
Freq | The frequency of any recommended action:
· D2 - Every 2 days
· SW - Semi-Weekly
· W1 - Weekly
· W2 - Bi-weekly
· M1 - Monthly
· M2 - Bi-monthly
· Q1 - Quarterly
· M4 - Tri-annual
· SA - Semi-annual
· A1 - Annual
· AX - Annual times a multiplier, X = 2 or greater
· M30 - Every 2.5 years
Freq Value | Decimal equivalent (based on Annual = 1.00) of the Freq.
· D2 - 0.005
· SW - 0.01
· W1 - 0.02
· W2 - 0.04
· M1 - 0.08
· M2 - 0.16
· Q1 - 0.25
· M4 - 0.33
· SA - 0.50
· A1 - 1.00
· AX - X.00
· M30 - 2.50
Basic Job Steps | Provides a summary statement of the actions to be performed for the indicated frequency.
Requirement | Rationale for frequencies and maintenance requirements, including but not limited to:
· Manufacturer’s recommendations
· Standards
· Codes
· Regulations
· Laws
Comments | Provides information from a MAR, Asset Management data and/or other information associated with the Asset Category.
Primary Job Plan Master | This column shows the primary Job Plans (JP) which are typically assigned to assets in this Asset Category. The Job Plan number indicated is a master designation which may be replicated where lower case x is shown. Multiple and/or other Job Plans may still be used due to specific requirements of any individual Asset.

## Comments-Updates
Asset Category | DATE | Maximo System | Comments
Isolation Disconnect Switch | 2022-05-12 | EHV | Per email from NASA SI JRIVERA & SHARP team, 4 assets M6-0996 updated from RTF to PM (Annual) MSE01013 MSE01014 MSE01015 MSE01016
Resistor | 2022-05-12 | ELV | PM Added for asset MSE01NGR-1 per SHARP team request.
Doors-Roll-up Manual | 2022-11-02 | STR | Per SE CWARNER Asset AB502010 (DOORS-ROOLUP-MANUAL-BOEING) Maintenance code will be changed from PM to RTF, per NASA concurrence.)
Toxic-HVC | 2023-05-22 | HVC | Added Asset Category Toxic-HVC. HVAC Sharp Team Concurrence Email Received by Asset Management on 05/22/2023.
Pump-Pad Mount-(CHW/CW)-Plant | 2023-09-06 | HVC | Removed Q1 PM requirement from Maintenance Plan Standard per HVAC SHARP Team Request (REV 15)
Pump-Vertical-(CHW/CW)-Plant | 2023-09-06 | HVC | Removed Q1 PM requirement from Maintenance Plan Standard per HVAC SHARP Team Request (REV 15)
Roof-BUR-A2 | 2023-09-06 | STR | Added New Asset Category with appended "-A2" per STR SHARP Team. Intent/Motive = Differentiate Roof-BUR assets that require A1 vs A2 Maintenance. (REV 15)
Roof-Metal-A2 | 2023-09-06 | STR | Added New Asset Category with appended "-A2" per STR SHARP Team. Intent/Motive = Differentiate Roof-Metal assets that require A1 vs A2 Maintenance. (REV 15)
Roof-Shingle-A2 | 2023-09-06 | STR | Added New Asset Category with appended "-A2" per STR SHARP Team. Intent/Motive = Differentiate Roof-Shingle assets that require A1 vs A2 Maintenance. (REV 15)
Roof-Single Ply-A2 | 2023-09-06 | STR | Added New Asset Category with appended "-A2" per STR SHARP Team. Intent/Motive = Differentiate Roof-Single ply assets that require A1 vs A2 Maintenance. (REV 15)
Bridge-Span Lift | 2023-09-13 | MEC | Updated required PM frequency to M2 - Bimonthly per SHARP Team (REV 16)
Pre-Action | 2024-02-15 | PSY | Removed Q1 PM requirement from Maintenance Plan Standard per FIRE SHARP Team Request (REV 17)
Channel Markers | 2024-04-02 | RDG | Removed Annual requirement from Maintenance Plan Standard per STRUCTURAL SHARP Team Request (REV 18)